## SUMMARY OF LOT-1(KPCIP-04)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILLS
BILL NO. | DESCRIPTION OF WORK | PC-1 Cost (Original) MRS 2020 | Amount (PKR)
1 | Distribution Chamber No. 1 | 0
2 | Plain Sedimentation Tank | #REF!
3 | Distribution Chamber No. 2 | #REF!
4 | Flash Mixer and Flocculation Chamber | #REF!
5 | Clarifier | #REF!
6 | Primary Sludge Pumping Station | #REF!
7 | Clarifier Sludge Pumping Station | #REF!
8 | Rapid Sand Filter | #REF!
9 | Sludge Thickener | #REF!
10 | Chlorine Contact Tank and TWT | #REF!
11 | Admin Building | #REF!
12 | Chemical Building | #REF!
13 | Chlorine Building | #REF!
14 | Sub Station Building | #REF!
15 | Electrical Control Room | #REF!
16 | Generator Room | #REF!
17 | Guard Room | #REF!
18 | Workshop | #REF!
19 | Operator Room | #REF!
20 | Main Gate & Boundry Wall | #REF!
21 | External Piping | #REF!
22 | External Electrification | #REF!
23 | Road Works | #REF!
23A | Operation & Maintinance of entire WTP & Client Staff Training | #REF!
24 | Storm Water Drainage System | #REF!
25 | External Sewerage System | #REF!
26 | Flood Protection (Embankment) | #REF!
27 | SCADA System | #REF!
28 | Belt Filter Press Sludge Pumping Station | #REF!
29 | Belt Filter Press Unit | #REF!
30 | Health & Safety (H&S), Environmental Management Plan (EMP) and Traffic Management Plan (TMP) Cost - (Provisional Sums) |  | 6410500
TOTAL AMOUNT (PKR) |  | #REF!

## 1-Summary (DC1)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 1: DISTRIBUTION CHAMBER NO. 1
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS
2 | MECHANICAL WORKS
TOTAL AMOUNT RS |  | 0
0

## 1-Civil (DC1)
BILL NO. 1 DISTRIBUTION CHAMBER-01 |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 1 DISTRIBUTION CHAMBER NO. 1
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material bymechanical means | M3 | 43.47
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 25
3 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 1.54
4 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 27
5 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | Per Cft | 7.15
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 56.56
7 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 12.88
8 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Tonne | 0.77
9 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 18.86
10 | 24-34 | Supplying and Fixing flat iron (2"x3/8") ladder for OHR, holes @ 15" c/c, steps of MS bars 5/8" i/d & paint complete | M | 4.14
11 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 25
12 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 25
13 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 25
14 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 25
15 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 12.4
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 1-Mechanical (DC1)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 1 DISTRIBUTION CHAMBER NO. 1
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Manual Penstock gate
Providing, installing and testing cast iron (CI) Penstocks (Manually Operated) in concrete structures, complete with sliding cover/gate & wedges, cover/gate guide & seating mechanism, stem, stem couplings, stem guides, top mounting brackets, thimbles andmanual gate lifting assembly, including all jointing, fixing, sealing & installation accessories, initial lubricant charge, all painting & coatings, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows:
|  | Penstock Gate Size with clear opening (1050mm x 1050mm) | Each | 2 |  |  | 0
2 | NS-2 | Temperature sensor
|  | Providing, installing, testing and commissioning water temperature sensor (Max water Temperature: 40OC) in Distribution chamber, of internationally reputed approved make, complete with on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
3 | NS-3 | pH Meter
|  | Providing, installing, testing and commissioning water pH Meter (Range: 0 – 14.00 pH, Max water Temperature: 40OC) in Distribution Chamber, of internationally reputed approved make, complete with pH probe/sensor, relays,on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
4 | NS-4 | TSS Sensor
|  | Providing, installing, testing and commissioning TSS sensor (with measuring range of 0.001 - 500g/l, Max water Temperature: 40OC) in Distribution chamber, of internationally reputed approved make, complete with on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 2-Summary (PST)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 2: PLAIN SEDIMENTATION TANK (2 No's)
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0
0
Amount (PKR)

## 2-Civil (PST)
BILL NO.3 PLAIN SEDIMENTATION TANK (2 No's) |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 2: PLAIN SEDIMENTATION TANK (2 No's)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 2415.05 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 555.46 |  |  | 0
3 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 120.16 |  |  | 0
4 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 124.71 |  |  | 0
5 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 432.86 |  |  | 0
6 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 1776.72 |  |  | 0
7 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 3589.95 |  |  | 0
8 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 157.88 |  |  | 0
9 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 555.46 |  |  | 0
10 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 555.46 |  |  | 0
11 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 555.46 |  |  | 0
12 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 555.46 |  |  | 0
13 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 357.67 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 2-Mechanical (PST)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 2: PLAIN SEDIMENTATION TANK (2 No's)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | 24-30-b-12 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects except excavation. (250 mm dia) PN-10 | m | 40 |  |  | 0
3 | NS-1 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 (800mm) | m | 50 |  |  | 0
4 | NS-2 | Providing cutting, fabricating and fixing in position SS scum and weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification | m | 65.9988 |  |  | 0
5 | NS-3 | Sludge Scrappers
Providing, installing, testing and commissioning Mechanical Sludge Scraper (End-Driven, Rotating Half-Bridge type, Peripheral Speed: 1-2 m/min), of internationally reputed approved make, complete with the main bridge structure with decking (Min Width: 1000 mm) & safety handrails (Min Height: 1100 mm), scraper blades (discontinuous, fish bone type, furnished with sweeping strip of EPDM)& their support structure, central support/bearing unit, current collector unit, end drive unit with motor, motor starter, reduction gearbox& wheels, obstacle detection switch, electric cable & conduit from current collector unit to end drive unit, inlet drum, scum skimmer, scum collection box, scum outflow pipe & valved outlet, with all the submerged/wetted components to be of stainless steel (Grade 316) and other structural components to be of carbon steel (approved epoxy coated), including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Primary Sedimentation Tanks (Internal Diameter: 21.4 m, Side Depth: 4.665 m) | Each | 2 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 3-Summary(DC#2)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 3: DISTRIBUTION CHAMBER NO. 2
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0
0

## 3-Civil(DC#2)
BILL NO. 4 DISTRIBUTION CHAMBER BETWEEN PST AND FLASH MIXER |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 3: DISTRIBUTION CHAMBER NO. 2
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material bymechanical means | M3 | 150.31 |  |  | 0
2 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 2.67 |  |  | 0
3 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 96 |  |  | 0
4 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 16.88 |  |  | 0
5 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 162.55 |  |  | 0
6 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 20 |  |  | 0
7 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Tonne | 0.77 |  |  | 0
8 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 26 |  |  | 0
9 | 24-34 | Supplying and Fixing flat iron (2"x3/8") ladder for OHR, holes @ 15" c/c, steps of MS bars 5/8" i/d & paint complete | M | 3.6 |  |  | 0
10 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 75.16 |  |  | 0
11 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 75.16 |  |  | 0
12 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 75.16 |  |  | 0
13 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 75.16 |  |  | 0
14 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 12.4 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 3-Mechanical(DC#2)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 3: DISTRIBUTION CHAMBER NO. 2
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ECHANICAL WORKS
1 | NS-1 | Manual Penstock Gate
Providing, installing and testing cast iron (CI) Penstocks (Manually Operated) in concrete structures, complete with sliding cover/gate & wedges, cover/gate guide & seating mechanism, stem, stem couplings, stem guides, top mounting brackets, thimbles andmanual gate lifting assembly, including all jointing, fixing, sealing & installation accessories, initial lubricant charge, all painting & coatings, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows:
|  | Penstock Gate Size with clear opening (1050mm x 1050mm) | Each | 4 |  |  | 0
2 | NS-2 | Temperature sensor
|  | Providing, installing, testing and commissioning water temperature sensor (Max water Temperature: 40OC) in Distribution chamber, of internationally reputed approved make, complete with on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
3 | NS-3 | pH Meter
|  | Providing, installing, testing and commissioning water pH Meter (Range: 0 – 14.00 pH, Max water Temperature: 40OC) in Distribution Chamber, of internationally reputed approved make, complete with pH probe/sensor, relays,on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
4 | NS-4 | TSS Sensor
|  | Providing, installing, testing and commissioning TSS sensor (with measuring range of 0.001 - 500g/l, Max water Temperature: 40OC) in Distribution chamber, of internationally reputed approved make, complete with on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 1 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 4-Summary (FM & FC)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 4: FLASH MIXER & FLOCCULATION CHAMBER
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0
0

## 4-civil (FM & FC)
BILL NO.5 FLOCCULATION CHAMBER AND FLASH MIXER |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 4: FLASH MIXER & FLOCCULATION CHAMBER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material bymechanical means | M3 | 2994.46 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 1497.23 |  |  | 0
2 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 85.56 |  |  | 0
3 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 757.43 |  |  | 0
4 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 320.84 |  |  | 0
5 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 2070.28 |  |  | 0
6 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Tonne | 24.66 |  |  | 0
7 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 199.4 |  |  | 0
8 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 321.8 |  |  | 0
9 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 1497.23 |  |  | 0
10 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 1497.23 |  |  | 0
11 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 1497.23 |  |  | 0
12 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 1497.23 |  |  | 0
13 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 571.31 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 4-Mechanical (FM & FC)
BILL NO.5 FLOCCULATION CHAMBER AND FLASH MIXER |  |  |  |  | 1.03
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 4: FLASH MIXER & FLOCCULATION CHAMBER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | FLASH MIXER
Providing, installing, testing and commissioning Mechanical Mixers (vertical-shaft, single impeller, pitched blade or propeller type, 3-4 blades), of internationally reputed approved make, complete with motor (4 pole, installed power to be determined by the manufacturer), gear box, motor starter, support base/frame, shaft, impeller and canopy, with all the submerged/wetted components to be of stainless steel (Grade 316), including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Flash Mixer Tanks (Imparted Mixing Power: 16 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 1.0 – 1.5 m) | Each | 4 |  |  | 0
2 | NS-2 | FLOCCULATOR
Providing, installing, testing and commissioning Mechanical Flocculators/Mixers (vertical-shaft, flat blade/paddle type), of internationally reputed approved make, complete with motor (4 pole, installed power to be determined by the manufacturer), gear box, motor starter, support base/frame, shaft, blades/paddles, connecting arms and canopy, with all the submerged/wetted components to be of stainless steel (Grade 316), including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Flocculation Chambers (Imparted Mixing Power: 1.4 kW, Rotational Speed: 5 – 15 RPM, Turbine Diameter: Min 3.4) | Each | 8 |  |  | 0
3 | NS-3 | pH Meter
|  | Providing, installing, testing and commissioning water pH Meter (Range: 0 – 14.00 pH, Max water Temperature: 40OC) in Flash mixer, of internationally reputed approved make, complete with pH probe/sensor, relays,on-site LCD display unit(with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | Each | 4 |  |  | 0
4 | NS-4 | Providing cutting, fabricating and fixing in position weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification. | M | 3.7 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 5-Summary (Clarifier)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 5: CLARIFIER TANK (04 No's)
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 5-Civil (Clarifier)
BILL NO. 6 SEDIMENTATION/ CLARIFIER TANK |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 5: CLARIFIER TANK (04 No's)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 10923.08 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 2184.62 |  |  | 0
3 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 523.38 |  |  | 0
4 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 620.37 |  |  | 0
5 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 1500.28 |  |  | 0
6 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 4771.88 |  |  | 0
7 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 10190.51 |  |  | 0
8 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 494.96 |  |  | 0
9 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Tonne | 1.54 |  |  | 0
10 | 24-30-b-10 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects (160 mm dia) PN-10 | M | 20 |  |  | 0
11 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 2512.31 |  |  | 0
12 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 2512.31 |  |  | 0
13 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 2512.31 |  |  | 0
14 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 2512.31 |  |  | 0
15 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 1872.25 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 5-Mechaical (Clarifier)
BILL NO. 6 SEDIMENTATION/ CLARIFIER TANK |  |  |  |  | 1.03
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 5: CLARIFIER TANK (04 No's)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | 24-30-b-10 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects (160 mm dia) PN-10 | M | 80 |  |  | 0
2 | NS-1 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 1000mm ( including fittings as Bends etc) | M | 150 |  |  | 0
3 | NS-2 | Providing cutting, fabricating and fixing in position SS scum and weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification | M | 280.34 |  |  | 0
4 | NS-3 | Sludge Scrappers
|  | Providing, installing, testing and commissioning Mechanical Sludge Scraper (End-Driven, Rotating Half-Bridge type, Peripheral Speed: 1-2 m/min), of internationally reputed approved make, complete with the main bridge structure with decking (Min Width: 1000 mm) & safety handrails (Min Height: 1100 mm), scraper blades (discontinuous, fish bone type, furnished with sweeping strip of EPDM)& their support structure, central support/bearing unit, current collector unit, end drive unit with motor, motor starter, reduction gearbox& wheels, obstacle detection switch, electric cable & conduit from current collector unit to end drive unit, inlet drum, scum skimmer, scum collection box, scum outflow pipe & valved outlet, with all the submerged/wetted components to be of stainless steel (Grade 316) and other structural components to be of carbon steel (approved epoxy coated), including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract, as follows: | EACH | 4 |  |  | 0
In Clarifier (Internal Diameter: 33.75 m, Side Depth: 4.665 m)
SUB TOTAL MECHANICAL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 6-Summary (Pri-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 6: PRIMARY SLUDGE PUMPING STATION (02)
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 6-Civil (Pri-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 6: PRIMARY SLUDGE PUMPING STATION (02)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-b-ii | Structural Excavation in Common Material by mechanical means | M3 | 52.9 |  |  | 0
2 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 19.14 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 26.45 |  |  | 0
4 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 8.25 |  |  | 0
5 | 06-07-d-01 | Reinforced cement concrete work as in dams, spillways, weirs, barrages, cross drainage works and other hydraulic structures using crushed stone aggregate(screening & washing) and coarse sand i/c cost of all labour and material and all kinds of form works, moulds, shuttering lifting/pumping, curing, rendering and finishing the exposed surface, cast in situ/precast excluding the cost of steel reinforcement and labour for bending binding also excludig cost of additives which have to be paid separately. (1:1:2) | M3 | 7.68 |  |  | 0
6 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 18.15 |  |  | 0
7 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 10.62 |  |  | 0
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 69.99 |  |  | 0
9 | 07-05-a-03 | 1st class brick work in ground floor Cement, sand mortar 1:4 | M3 | 17.47 |  |  | 0
10 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | M2 | 87.36 |  |  | 0
11 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 87.36 |  |  | 0
12 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 | M2 | 87.36 |  |  | 0
13 | 11-10-a | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:2) | M2 | 87.36 |  |  | 0
14 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 23 |  |  | 0
15 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 23 |  |  | 0
16 | 09-01 | First class tile roofing including earth, mud plaster, gobri leeping, cement plaster etc complete | M2 | 52.08 |  |  | 0
17 | 09-13 | 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft | M2 | 52.08 |  |  | 0
18 | 06-28 | Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) under cement concete. | M2 | 52.08 |  |  | 0
19 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 7.2 |  |  | 0
20 | 25-45-b | Supplying and Fixing 18 SWG MS Sheet Gate with angle iron frame (2"x2"x3/16") with side window, lock, painting etc | M2 | 7.2 |  |  | 0
21 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 26.45 |  |  | 0
22 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 26.45 |  |  | 0
23 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 26.45 |  |  | 0
24 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 26.45 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 6-Mechanical (Pri-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 6: PRIMARY SLUDGE PUMPING STATION (02)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Primary Sludge Pumps
Providing, installing, testing and commissioning Sludge Pumps (horizontal-shaft, end-suction, non-clogging/solids-handling, centrifugal type, Min Free Passage Size: 15-50 mm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Efficiency class IE3), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Primary Sludge (Max Concentration: 5 %) Pumps: Capacity: 70 m3/h, Head: 10 m | No | 4 |  |  | 0
2 | NS-2 | Flow Meter
|  | Providing, installing, testing and commissioning Water Flow Meter (Electromagnetic type, Range: 0 to 2000 m3/h, Accuracy: ± 0.5%, PN 16, Max Water Temperature: 40OC) on pipeline (HDPE, DN 150), of internationally reputed approved make, complete with meter, relays,on-site LCD display unit (with adjustable backlight and contrast)& its mounting arrangement (in stainless steel, Grade 316), display unit cabinet (painted metallic box with glazed front door), all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | No | 2 |  |  | 0
3 | NS-3 | DUCTILE IRON PIPE (DI PIPE)
Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron Pipe class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
|  | DI Pipe 150mm | M | 30 |  |  | 0
4 | NS-4 | Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron (cast on flange) specials (such as bend, tee, cross collar, reducer, tail piece, flanged spigot, cap, flanged socket, taper, angle branch, plug etc) class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
a) |  | Bend 90°
|  | 150 mm | No | 16 |  |  | 0
b) |  | DI TEE
|  | 150mm x 150mm | No | 6 |  |  | 0
c) |  | DI REDUCER
|  | 150mm | No | 4 |  |  | 0
(CI) Check Valves ( 150mm )
5 | NS-5 | Providing, installing and testing cast iron (CI) Check Valves (Swing type, Flanged, BS 5153, PN 10) on pipelines, of internationally reputed approved make, including gaskets, steel nuts & bolts and other jointing accessories, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows: | No | 4 |  |  | 0
SLUICE VALVE ( 150mm )
6 | NS-6 | Sluice Valves with all acessories complete in all respect for various pipe sizes as shown on the drawings | No | 4 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 6-Electrical(Pri-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 6: PRIMARY SLUDGE PUMPING STATION (02)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 146.34 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 73.17 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 256.1 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 170.73 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 268.3 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 178.87 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
A.05 |  | Exhaust Fan Point
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc: 3/4" i/d | M | 36.59 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 82.32 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 54.88 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 73.17 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 146.34 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 97.56 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 195.12 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 14 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 256.1 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 170.73 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 341.47 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 14 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.18 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.79 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 97.57 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 4 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | Nos. | 12 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 24 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 8 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | Nos. | 8 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | Nos. | 2 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | M | 18.3 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, DBLP-G2, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 2 |  |  | 0
A.17 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 4 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 7-Summary (Clarif-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 7: CLARIFIER PUMPING STATION (04)
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 7-Civil (Clarif-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 7: CLARIFIER PUMPING STATION (04)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-b-ii | Structural Excavation in Common Material by mechanical means | M3 | 105.8 |  |  | 0
2 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 38.28 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 52.9 |  |  | 0
4 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 16.5 |  |  | 0
5 | 06-07-d-01 | Reinforced cement concrete work as in dams, spillways, weirs, barrages, cross drainage works and other hydraulic structures using crushed stone aggregate(screening & washing) and coarse sand i/c cost of all labour and material and all kinds of form works, moulds, shuttering lifting/pumping, curing, rendering and finishing the exposed surface, cast in situ/precast excluding the cost of steel reinforcement and labour for bending binding also excludig cost of additives which have to be paid separately. (1:1:2) | M3 | 25.83 |  |  | 0
6 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 25.83 |  |  | 0
7 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 21.24 |  |  | 0
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 139.98 |  |  | 0
9 | 07-05-a-03 | 1st class brick work in ground floor Cement, sand mortar 1:4 | M3 | 34.94 |  |  | 0
10 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | M2 | 174.72 |  |  | 0
11 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 174.72 |  |  | 0
12 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 | M2 | 174.72 |  |  | 0
13 | 11-10-a | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:2) | M2 | 174.72 |  |  | 0
14 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 46 |  |  | 0
15 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 46 |  |  | 0
16 | 09-01 | First class tile roofing including earth, mud plaster, gobri leeping, cement plaster etc complete | M2 | 104.16 |  |  | 0
17 | 09-13 | 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft | M2 | 104.16 |  |  | 0
18 | 06-28 | Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) under cement concete. | M2 | 104.16 |  |  | 0
19 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 14.4 |  |  | 0
20 | 25-45-b | Supplying and Fixing 18 SWG MS Sheet Gate with angle iron frame (2"x2"x3/16") with side window, lock, painting etc | M2 | 14.4 |  |  | 0
21 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 52.9 |  |  | 0
22 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 52.9 |  |  | 0
23 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 52.9 |  |  | 0
24 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 52.9 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 7-Mech (Clarif-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 7: CLARIFIER PUMPING STATION (04)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Clarifier Sludge Pumps
Providing, installing, testing and commissioning Sludge Pumps (horizontal-shaft, end-suction, non-clogging/solids-handling, centrifugal type, Min Free Passage Size: 15-50 mm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Efficiency class IE3), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Primary Sludge (Max Concentration: 5 %) Pumps: Capacity: 70 m3/h, Head: 10 m | No | 8 |  |  | 0
2 | NS-2 | Flow Meter
|  | Providing, installing, testing and commissioning Water Flow Meter (Electromagnetic type, Range: 0 to 2000 m3/h, Accuracy: ± 0.5%, PN 16, Max Water Temperature: 40OC) on pipeline (HDPE, DN 150), of internationally reputed approved make, complete with meter, relays,on-site LCD display unit (with adjustable backlight and contrast)& its mounting arrangement (in stainless steel, Grade 316), display unit cabinet (painted metallic box with glazed front door), all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | No | 4 |  |  | 0
3 | NS-3 | DUCTILE IRON PIPE (DI PIPE)
Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron Pipe class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
|  | DI Pipe 150mm | M | 30 |  |  | 0
4 | NS-4 | Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron (cast on flange) specials (such as bend, tee, cross collar, reducer, tail piece, flanged spigot, cap, flanged socket, taper, angle branch, plug etc) class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
a) |  | Bend 90°
|  | 150 mm | No | 16 |  |  | 0
b) |  | DI TEE
|  | 150mm x 150mm | No | 6 |  |  | 0
c) |  | DI REDUCER
|  | 150mm | No | 4 |  |  | 0
5 | NS-5 | (CI) Check Valves ( 150mm )
|  | Providing, installing and testing cast iron (CI) Check Valves (Swing type, Flanged, BS 5153, PN 10) on pipelines, of internationally reputed approved make, including gaskets, steel nuts & bolts and other jointing accessories, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows: | No | 8 |  |  | 0
6 | NS-6 | SLUICE VALVE ( 150mm )
|  | Sluice Valves with all acessories complete in all respect for various pipe sizes as shown on the drawings | No | 8 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 7-Electrical (Clarif-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 7: CLARIFIER PUMPING STATION (04)
1 | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 146.34 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 73.17 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 256.1 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 170.73 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 268.3 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 178.87 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 36.59 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 82.32 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 54.88 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 73.17 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 146.34 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 97.56 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 195.12 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 14 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 256.1 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 170.73 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 341.47 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 14 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.18 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.79 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 97.57 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 4 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | Nos. | 12 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 24 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 8 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | No | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 8 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | Nos. | 2 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | M | 18.3 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, DBLP-G2, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 2 |  |  | 0
A.17 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 4 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 8-Summary(RSF)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 8: RAPID GRAVITY FILTER
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 8-Civil (RSF)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 8: RAPID GRAVITY FILTER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 15374.03 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 7687.02 |  |  | 0
3 | 06-05-h | Plain Cement Concrete including placing,compacting, finishing & curing (Ratio 1:3:6) | M3 | 301.87 |  |  | 0
4 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 4805.72 |  |  | 0
5 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 1509.33 |  |  | 0
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 12124.9 |  |  | 0
7 | 23-03-c-07 | Providing & laying R.C.C. pipe sewers, moulded with cement concrete 1:1-1/2:3 conforming to ASTM specification C-76-79, Class IV, Wall B, including carriage, lowering in trenches to correct alignment and grade, jointing with rubber ring, cutting pipes where necessary, testing, etc. complete:- 30" i/d, Wall B | M | 25 |  |  | 0
8 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 1478.07 |  |  | 0
9 | 07-05-a-03 | 1st class brick work in ground floor Cement, sand mortar 1:4 | M3 | 274.36 |  |  | 0
10 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | M2 | 1316.79 |  |  | 0
11 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 1316.79 |  |  | 0
12 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 | M2 | 1034.52 |  |  | 0
13 | 11-10-a | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:2) | M2 | 136.17 |  |  | 0
14 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 470.8 |  |  | 0
15 | 24-34 | Supplying and Fixing flat iron (2"x3/8") ladder for OHR, holes @ 15" c/c, steps of MS bars 5/8" i/d & paint comple (for screen chamber) | M | 49.75 |  |  | 0
16 | 09-01 | First class tile roofing including earth, mud plaster, gobri leeping, cement plaster etc complete | M2 | 1214.9 |  |  | 0
17 | 09-13 | 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft | M2 | 1214.9 |  |  | 0
18 | 06-28 | Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) under cement concete. | M2 | 1214.9 |  |  | 0
19 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 24 |  |  | 0
20 | 25-45-b | Supplying and Fixing 18 SWG MS Sheet Gate with angle iron frame (2"x2"x3/16") with side window, lock, painting etc | M2 | 17.55 |  |  | 0
21 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 35.1 |  |  | 0
22 | 06-08-a | Supply & fabricate M.S. reinforcement for cement concrete (Plain bars) (Rungs for UGWT) | 100 Kg | 4 |  |  | 0
23 | 14-37-c | Supply and Fixing cast iron (CI) manhole cover with frame etc (Heavey Type) of approved uality complete: 24" (610 mm) dia | Each | 6 |  |  | 0
24 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 7687.02 |  |  | 0
25 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 7687.02 |  |  | 0
26 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 7687.02 |  |  | 0
27 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 7687.02 |  |  | 0
28 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 1929.2 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 8-Mechanical (RSF)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 8: RAPID GRAVITY FILTER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MEACHANICAL WORKS
1 | NS-1 | Providing cutting, fabricating and fixing in position SS scum and weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification | M | 61.3 |  |  | 0
2 | NS-2 | Backwash Pumps
Providing, installing, testing and commissioning backwash Pumps (vertical-shaft, non-clogging/solids-handling, submersible, centrifugal type), of internationally reputed approved make, complete with pump, motor (4-pole), automatic liquid level-controlled switching device (ultrasonic sensor type) and starter, with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Capacity: 14.5 ft3/s, Head: 55 ft | No. | 6 |  |  | 0
3 | NS-3 | Motorized Penstock Gates
Providing, installing, testing and commissioning cast iron (CI) Penstocks (Motor Operated, with Manual Override) in concrete structures, of internationally reputed approved make, complete withsliding cover/gate & wedges, cover/gate guide & seating mechanism, stem, stem couplings, stem guides, top mounting brackets, thimbles, manual gate lifting assembly, geared motor, motor starter and on/off control device,including all jointing, fixing, sealing& installation accessories,initial lubricant charge, all painting & coatings, with all the exposed ferrous surfaces to be epoxy coated, and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | 1000mm x 600mm (For all installation depths) | No. | 20 |  |  | 0
|  | 450mm x 450mm (For all installation depths) | No. | 20 |  |  | 0
4 | NS-4 | Top-Running Double-Girder Bridge Cranes
Providing, installing, testing and commissioning Top-Running Double-Girder Bridge Cranes, of internationally reputed approved make, complete with all its moving components, drives, drive controls, safety mechanisms, cables, cables collapsing mechanisms, operation-control equipment, and side rails, to be supported on the structure, including all jointing, fixing & installation accessories, initial charging of lubricants, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Capacity: 5 Tons | Each | 2 |  |  | 0
5 | NS-5 | Air Blowers
Providing, installing, testing and commissioning Air Blowers (Screw Type) for Backwashing in rapid sand filters, of internationally reputed approved make, complete with 3-phase motor, support base/frame, sound absorber canopy (Maximum Sound Level: 75 dB-A), silencer, air filter, pressure gauge, check valve, blow off valve, safety valve, inlet & outlet connections, all necessary devices for automatic switching ON/OFF of blower, motor control unit (MCU, in painted metallic box, complete with starter and all the required control, relay, monitoring and protection devices) and electrical & control cables (between blower and MCU), including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Rapid Gravity Filters; Air Flow rate: 2700 m3/hr, Differential Pressure = 1bar | No. | 4 |  |  | 0
6 | NS-6 | Ductile Iron (DI) Pipe
Providing, laying, cutting, jointing, testing and disinfecting DI PIPE in filteration assembly, complete in all respects.( including fittings as Bends etc)
a) |  | 200mm | M | 192 |  |  | 0
b) |  | 300mm | M | 48 |  |  | 0
c) |  | 600mm | M | 168 |  |  | 0
7 | NS-7 | Motorized Butterfly valve
|  | 200mm | No. | 20 |  |  | 0
|  | 300mm | No. | 20 |  |  | 0
|  | 600mm | No. | 40 |  |  | 0
9 | NS-9 | Ultrasonic Level Sensor
|  | Providing, installing, testing and commissioning Ultrasonic level sensors ( Max Water Temperature: 40C, With automatic temperature compensation) in Rapid Sand Filtration Tank, of internationally reputed approved make, complete with on-site LCD display unit (with adjustable backlight and contrast), mounting arrangements (in stainless steel, Grade 316) for probe & display unit, display unit cabinet (painted metallic box with glazed front door),electric cable & conduit between probe & display unit, all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | No. | 20 |  |  | 0
6 | NS-6 | Provide , Place & compact filter media containing layers of silica sand (800mm depth) and well graded gravel (460mm depth) as per given specification and drawing complete in all respect | per sq.m | 1250.7 |  |  | 0
7 | NS-7 | Supply, installation, testing and commissioning of Filter Nozzles with threaded sleeves to be embedded into precast plenum floor in PP / PVDF / FRP material of construction complete in all respect s as per drawings and specifications. | No. | 38880 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 8-Electrical(RSF)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 8: RAPID GRAVITY FILTER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
1 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 97.56 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
2 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 146.34 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 48.78 |  |  | 0
3 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 390.24 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 130.08 |  |  | 0
4 |  | Gang Light Control Switches
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 8 |  |  | 0
5 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 109.76 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 36.59 |  |  | 0
6 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 439.02 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 146.34 |  |  | 0
7 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
8 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 329.27 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 109.76 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 109.76 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 18 |  |  | 0
9 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 329.27 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 109.76 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 109.76 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 18 |  |  | 0
10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 4 |  |  | 0
11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 40 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 12 |  |  | 0
12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 8 |  |  | 0
13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 12 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | Nos. | 12 |  |  | 0
14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, DBLP-G2, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 2 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 42.68 |  |  | 0
15 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 4 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 4 |  |  | 0
16 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 9-Summary (ST)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 9: SLUDGE THICKENER
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 9-Civil (ST)
BILL NO. 7 SLUDGE THICKNER |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 9: SLUDGE THICKENER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 4355.63 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 871.13 |  |  | 0
2 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 54 |  |  | 0
3 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 80.04 |  |  | 0
4 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 255.86 |  |  | 0
5 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | Per Cft | 420.39 |  |  | 0
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 955.41 |  |  | 0
7 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 83.25 |  |  | 0
8 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Tonne | 1.54 |  |  | 0
9 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 59.6 |  |  | 0
10 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 871.13 |  |  | 0
11 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 871.13 |  |  | 0
12 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 871.13 |  |  | 0
13 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 871.13 |  |  | 0
14 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 169.56 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 9-Mechanical (ST)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 9: SLUDGE THICKENER
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | 24-30-b-10 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects (160 mm dia) PN-10 | M | 25 |  |  | 0
2 | 24-30-b-12 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects (250 mm dia) PN-10 | M | 45 |  |  | 0
3 | NS-1 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 710mm ( including fittings as Bends etc) | M | 30 |  |  | 0
4 | NS-2 | Providing cutting, fabricating and fixing in position SS scum and weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification | M | 36.14 |  |  | 0
5 | NS-3 | Sludge Scrappers
|  | Providing, installing, testing and commissioning Mechanical Sludge Scraper (End-Driven, Rotating Half-Bridge type, Peripheral Speed: 1-2 m/min), of internationally reputed approved make, complete with the main bridge structure with decking (Min Width: 1000 mm) & safety handrails (Min Height: 1100 mm), scraper blades (discontinuous, fish bone type, furnished with sweeping strip of EPDM)& their support structure, central support/bearing unit, current collector unit, end drive unit with motor, motor starter, reduction gearbox& wheels, obstacle detection switch, electric cable & conduit from current collector unit to end drive unit, inlet drum, scum skimmer, scum collection box, scum outflow pipe & valved outlet, with all the submerged/wetted components to be of stainless steel (Grade 316) and other structural components to be of carbon steel (approved epoxy coated), including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract, as follows: | EACH | 1 |  |  | 0
In Sludge Thickener (Internal Diameter: 18.0 m, Side Depth:4.5m)
6 | NS-4 | Tractor with Trolly
|  | Providing Tractor with trolly at site including registration or any other Govt dues with following details The tractor having capacity of 75HP and should be 4WD with trolly 7Cu.m capacity as per given specification | Each | 2 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 10-Summary(CCT & TWT)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 10: CHLORINE CONTACT TANK & TREATED WATER TANK
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 10-Civil (CCT &TWT)
BILL NO. 1 DISTRIBUTION CHAMBER-01 |  |  |  |  | 1.08
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 10: CHLORINE CONTACT TANK & TREATED WATER TANK
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 58174.05 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 14543.5125 |  |  | 0
3 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 956.66 |  |  | 0
4 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 5304.5 |  |  | 0
5 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 4632.29 |  |  | 0
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 19078.64 |  |  | 0
7 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 615 |  |  | 0
8 | 25-33-a | Providing and fixing terrace railing 2" i/d conduit pipe 16 SWG, welded with 5/8" x 5/8" square bar 2.75 ft. high fixed at 5" centre to centre, in RCC slab with suitable arrangement, complete in all resppects as per design and drawing. | M | 338.3 |  |  | 0
8a | 24-34 | Supplying and Fixing flat iron (2"x3/8") ladder for OHR, holes @ 15" c/c, steps of MS bars 5/8" i/d & paint complete | M | 3.96 |  |  | 0
9 | 25-10&11 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Steel stair including duly painting red oxide) | Ton | 0.58 |  |  | 0
10 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 14543.5125 |  |  | 0
11 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 14543.5125 |  |  | 0
12 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 14543.5125 |  |  | 0
13 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 14543.5125 |  |  | 0
14 | 13-08-a | Bitumen coating to plastered/cement concrete surface: 20 lbs per 100 sft | m2 | 2048.65 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0
Note on F1: Author: factor for Kohat

## 10-Mechanical (CCT & TWT)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 10: CHLORINE CONTACT TANK & TREATED WATER TANK
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Providing, installing and testing cast iron (CI) Penstocks (Manually Operated) in concrete structures, of internationally reputed approved make, complete with sliding cover/gate & wedges, cover/gate guide & seating mechanism, stem, stem couplings, stem guides, top mounting brackets, thimbles andmanual gate lifting assembly, including all jointing, fixing, sealing & installation accessories, initial lubricant charge, all painting & coatings, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows:
|  | 1050 mm x 1050 mm(for all Installation Depths) | No. | 2 |  |  | 0
2 | NS-2 | Providing cutting, fabricating and fixing in position weir plates 5mm thick welded with SS angle and embedded into concrete with bolt and nut @ 500mm c/c complete in all respect as per given drawing and specification. | M | 60 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 11-Summery (AB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 11: ADMIN BUILDING
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
4 | PLUMBING WORKS | 0
TOTAL AMOUNT RS |  | 0

## 11-Civil (AB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 11: ADMIN BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-b-i | Structural Excavation in Common Material by mechanical means | M3 | 315.92 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 210.61 |  |  | 0
Anti-Termite
3 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 370.57 |  |  | 0
Plain and Reinforement Concrete
4 | 06-03-b | Cement Concrete (brick/stone ballast, 1.5" to 2"/nullah shingle well graded and cleaned) in foundation & plinth (Ratio 1:4:8) | M3 | 5.28 |  |  | 0
5 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 24.52 |  |  | 0
GROUND FLOOR
6 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 43.4 |  |  | 0
FIRST FLOOR
7 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 37.06 |  |  | 0
MUMTY
8 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 5.04 |  |  | 0
Steel Reinforcement
9 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 26.67 |  |  | 0
10 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 30.5 |  |  | 0
11 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 55.23 |  |  | 0
Brick Work
12 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 17.32 |  |  | 0
GROUND FLOOR
13 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 61.82 |  |  | 0
FIRST FLOOR
14 | 07-05-a-04 | 1st class brick work in first floor Cement, sand mortar 1:5 | M3 | 66.62 |  |  | 0
MUMTY
15 | 07-05-a-04 | 1st class brick work in second floor Cement, sand mortar 1:5 | M3 | 12.17 |  |  | 0
Flooring
16 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 10.49 |  |  | 0
17 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 18.37 |  |  | 0
18 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 9.16 |  |  | 0
19 | 10-55-g | Providing and Fixing of Porcelain Floor Tile 24" x 24" of approved quality | M2 | 143.12 |  |  | 0
20 | 10-51 | Providing and Fixing of Ceramic Tiles 12"×24" of Imported Approved Quality with jointing and finishing | M2 | 22.27 |  |  | 0
21 | 10-42 | Providing and fixing on walls1/4"(6mm approx.) thick of imported first grade ceramic tiles of size 24 in x 24 in of approved colour on walls, over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | M2 | 116.3 |  |  | 0
Surface Rendring
22 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 173.77 |  |  | 0
23 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 1017.88 |  |  | 0
24 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 338.66 |  |  | 0
Wood Work
25 | 12-49-c | First class deodar wood wrought joinery in doors and windows etc. panelled or panelled or glazed or fully glazed fixed in position including chowkhat, holdfast, hinges, tower bolt rubber stop cleats/G I clamp, handles and chord with hooks etc. complete (excluding sliding bolts or lock) : 1½" (40mm) thick. | M2 | 5.38 |  |  | 0
26 | 12-56-c | Providing and fixing 1.5" (38 mm) thick pressed veneered door shutters fully flushed with First class wood veneering on all faces and sides fixed over partal wood cavited core and frame work of not less than 4" (100mm) wide strips all round with approved iron hinges, tower bolts as required. | M2 | 33.94 |  |  | 0
27 | 12-57-a | Providing and fixing single leaf steel door with frame fully panelled with M.S sheet 16 gauge (1.59mm) painted with two coats of red oxide paint with brass fitting of approved make including cost of fabrication, iron lugs, cutting holes and making good the damages to walls | M2 | 2.35 |  |  | 0
28 | 12-70-a | Supply and Fixing MS Sheet 16 guage(10'' x 2'') box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc | M | 81.84 |  |  | 0
29 | 12-24-a-01 | providing/fixing approved quality Rim locks : Imported | Each | 13 |  |  | 0
30 | 12-22-a-01 | Providing and fixing sliding bolt to doors Iron sliding bolts : 10" long | Each | 8 |  |  | 0
31 | 12-21-b | P/F hydraulic Door Closer (Best Quality) | Each | 7 |  |  | 0
32 | 12-78-a | Kitchen Floor Cabinet as per MES Design/Specification. | M2 | 5.02 |  |  | 0
33 | 12-78-b | Kitchen Wall Cabinet as per MES Design/Specification. | M2 | 3.65 |  |  | 0
Painting and Warnishing
34 | 11-20-b | Providing and applying wall putty of 2mm thickness over plastered surface to prepare the surface even and smooth complete. | M2 | 1251.24 |  |  | 0
35 | 13-03-i | Providing and applying 3 coats of approved type of Plastic emulsion paint to Plastic surface as per manufucture specification. | M2 | 1251.24 |  |  | 0
36 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 355.59 |  |  | 0
37 | Ch-13 item 06 P-100 | Applying lacquer polish to wood work of any type | M2 | 78.63 |  |  | 0
38 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 4.7 |  |  | 0
Metal Work
39 | 12-66 | Supply and Fixing of double glazed aluminium (color as approved) Premium model (Gauge 2 mm) 4" sect. Sliding window, including all necessary fittngs and fly screen shutters complete. | M2 | 37.28 |  |  | 0
40 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | M2 | 18.56 |  |  | 0
41 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | M | 16 |  |  | 0
Roofing & Water Proofing
42 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 104.94 |  |  | 0
43 | 09-16 | Khuras on roof 2'x2'x6" | Each | 2 |  |  | 0
44 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 2 |  |  | 0
45 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 210.61 |  |  | 0
46 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 210.61 |  |  | 0
47 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 210.61 |  |  | 0
48 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 210.61 |  |  | 0
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 9.82 |  |  | 0
Entrance Steps / Podium
2 | N.S | Providing and fixing 3/4" thick pre-polished Granite Marble Slab uniform texture full width area above 2 sft laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges complete in all respect as approved / directed by The Engineer. | M2 | 3.22 |  |  | 0
Stair Steps
3 | N.S | Providing and laying Pre-polished Black Granite (supreme quality) slabs laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment, making rounding edge and chemical polishing etc; complete in all respect as per Specifications, and as per sample approved by The Engineer.
3.1 | a) | 3/4" thick Pre-polished Black Granite (supreme quality) one-piece slab of length and width as shown on drawings, over treads and projecting edge of treads will be doubled by bounding and rounded smooth of stairs and entrance steps. | M2 | 17.07 |  |  | 0
3.2 | b) | 1/2" thick Pre-polished Black Granite (supreme quality) slabs of length and height as shown on drawings, over risers of stairs and entrance steps. | M2 | 6.83 |  |  | 0
4 | N.S | Providing and laying Pre-polished Black Granite one-piece marble slabs Kitchen / Vanity Counter etc; laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment, making rounding edge and chemical polishing etc; complete in all respect, as per drawings and Specifications, sample as approved by The Engineer. | M2 | 3.65 |  |  | 0
Miscellenious
5 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 19.2 |  |  | 0
6 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 2 |  |  | 0
7 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 2 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 11-Mechanical (AB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 11: ADMIN BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | laboratory Equipments
|  | Providing laboratory equipment at water treatment plant site laboratory to check different water quality parameters.( i.e. Drying oven & sterilizers, Ultrasonic washers, Colony counter, Double beam spectrophotometer, Turbidity meter, pH meters,Conductivity meter, Refrigerator and medical freezer, Centrifuges, Nitrogen digestor and distillation apparatus, Jar testers, Furniture and glassware, Microscopes, and any equipment/instrument for testing of parameters specified by engineer.) | LS | 1 |  |  | 0
2 | NS-2 | Potable water Pumps
|  | Designing, manufacturing, testing at manufacturer's workshop, supplying at site, installaiton, testing, commissioning, gurantee and maintenance for one yerar during defect liability period of each item of Horizontal shaft split centrifugal pump including all accessories with suitable motor, control panel and delivery pipe, complete in all respects as per drawings and specificaitons. The pump and motor shall be of approved manufacturer. | No | 2 |  |  | 0
Capacity:17m3/hr, Head:20m
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 11-Electrical (AB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 11: ADMIN BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | m | 402.44 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | m | 100.61 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | m | 768.29 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | m | 256.1 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | m | 914.63 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | m | 304.88 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 10 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 6 |  |  | 0
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 14 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 12 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | m | 96.04 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | m | 32.01 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | m | 178.35 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | m | 59.45 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | m | 219.51 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | m | 73.17 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | m | 219.51 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | m | 73.17 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | m | 73.17 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 24 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | m | 402.44 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | m | 134.15 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | m | 134.15 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 22 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | m | 219.51 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | m | 73.17 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | m | 73.17 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 12 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | No | 27 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 48 |  |  | 0
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | No | 2 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | No | 27 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | No | 7 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | No | 13 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | No | 13 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | No | 1 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | m | 106.71 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-GF, DBLP-1F, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 2 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | m | 15.24 |  |  | 0
A.17 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 3 |  |  | 0
A.18 |  | Fire Alarm System
| 15-131-a | Supply, testing and commissioning of 2 core 1.5mm. Sqmm stranded copper conductor tin coated with drain PVC insulated wires 600/1000 V. grade, fire resistant, LSZH Cu Conductor to be pulled in already installed 20mm dia. heavy duty PVC conduit recessed in wall, columns, slab, floor or above false ceiling with all necessary fixing accessories as per site conditions | Point | 20 |  |  | 0
| 15-131-b | Supply, installation, testing & commissioning of Analogue Addressable Manual Call Point / Pull Station with Base and Back Box with Key UL Listed complete in all respects. | Each | 4 |  |  | 0
| 15-131-c | Supply, installation, testing & commissioning of Analogue Addressable Sounder with Flasher, 24 VDC, Mounting Base and with Base and Back Box with Key UL Listed complete in all respects. | Each | 4 |  |  | 0
| 15-131-d | Supply, installation, testing & commissioning of Analogue Addressable Optical Smoke Detector with Base; 24 VDC; UL LISTED, low voltage, solid state, Not Radio Active type, uni-polar and dual chamber with LED alarm indication to be installed on RCC slab, complete in all respects. | Each | 16 |  |  | 0
| 15-131-e | Supply, installation, testing & commissioning of Addressable Heat Detector | Each | 1 |  |  | 0
| 15-131-g | Supply, installation, testing & commissioning of Microprocessor based Fire Alarm Control Panel, suppression consisting of loops and can address around 125points, indicating circuits, including 2x12V VDC Batteries, suppression zone built in power supply, including stand by battery, alarm and trouble indication, silence alarm and reset system, general alarm and reset system, general alarm facility, complete in all respects. | Each | 1 |  |  | 0
A.19 |  | CCTV System
| 15-139-a | Supply and Installation of Outdoor True Day & Night Color Camera 1/3" CCD, 530TVL, 0 Lux, 49 IR LEDs, 2.8 to 10mm Auto Iris Varifocal Lens, IP66 Rating Outdoor Weatherproof Housing, DC12V/ AC24V, PAL, HCD-92534X-Honyewell completed in all respect | Each | 2 |  |  | 0
| 15-139-b | Supply and Installation of True Day & Night Color Indoor Camera 1/3" CCD, 550TVL, Color 0.3Lux & B/W 0.002Lux, Day/Night, DC12V/ AC24V, PAL, HCC-690P completed in all respect | Each | 4 |  |  | 0
| 15-140-b | Supply, installation, testing and commissioning of Patch Panel 24 Port Loaded with RJ-45 I/Os Suitable for CAT-VI FTP CABLE; Rack Mount, complete in all respects. | Each | 1 |  |  | 0
| 15-139-f | Supply Installation of 32-Channel Digital Video Recorder, real time display 400ips andwith Built-in DVD writer, XtraStor/MPEG4 compression,1TB,HDD,SATA port with remoteviewing and management software HNDR-E1648L-N-D-E,Honyewell.complated with all respect | Each | 1 |  |  | 0
| 15-141-a | Supply, installation, testing and commissioning of Cable Manager / Organizer | Each | 1 |  |  | 0
| 15-181 | Supply and installation of structure cable as required for CAT-6 PVC shielded cable in already installed Trunking/ conduit/ Channel , inducing Balun for vedio and power facility at both ends of cable to be provided. The CAT- 6 cable should be 3M Australian or equivalent, complete in all respects | m | 300 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | m | 300 |  |  | 0
A.20 |  | Telephone System.
| 15-138-a-03 | Supply and Installation of 50-Pair Telephone Junction Box with back mounting frame and connection strip Recessed in wall Type where shown on drawings, made of 16 SWG M.S. Sheet with hinged door. Completed in all respects | Each | 1 |  |  | 0
| 15-138-g | Supply and Erection of 3M Cat-6 Cable in 3/4",1"pvc conduit, complete in all respect | m | 455.79 |  |  | 0
| 15-138-j | Supply and Installation of Double Port Telephone outlet of CAT-5,1 x RJ-45 I/Os and back box of 16 SWG, complete in all respects | Each | 2 |  |  | 0
| 15-138-i | Supply and Installation of Single Port Telephone outlet of CAT-5,1 x RJ-45 I/Os and back box of 16 SWG, complete in all respects | Each | 23 |  |  | 0
| 15-138-k-01 | Supply installation, connection, testing and Commissioning of Telephone Exchange comparising 4 Trunk lines, 12 Digital Estentions, 200 Auto Dial Extention and attendeant console with UPS builtin 16+ 34 Kx-Txa 600. | Each | 1 |  |  | 0
A.21 |  | Computer System
| 15-136-c | Supply at site, installation, testing and commissioning of U/UTP, 4 pair Cat 6a (500 MHz) Network Cable supports (10 Giga) laid in PVC Conduit , with pure copper conductor PVC insulated PVC sheathed including cost of Single Shutter Face plate with UTP Cat-6a Keystone Jack with Back Box to be installed on walls, from Data Cabinet to Computer Points, PVC conduit & Cable tray. Complete in all respects. | Each | 23 |  |  | 0
| 15-136-b | Supply at site, installation, testing and commissioning of Layer 2 (Edge) Level Network Switch, Manageable for Data Rack, 24 Port Giga Ethernet (10/100/1000) with Copper & Fiber Uplink Ports (Support 04 Nos 1.0 Giga SFP Modules). 1.0 Gigabit uplink flexibility with Small Form-Factor Pluggable Plus (SFP+). 8 ports of Gigabit Ethernet for desktop connectivity, complete in all respects. | Each | 1 |  |  | 0
| 15-136-f | Supply at site, installation, testing and commissioning of data cabinet of approximate size as mentioned below, powder coated, having lockable glass door at front, 4 exhaust fans on top, suitable for under mentioned patch panels, consisting of the following voice and data points to be terminated on modular patch panel, including cost of power bus bar, input / output RJ-45 connectors suitable for Cat. 6a cables patch guides, patch cords, both for Voice and Data, all necessary accessories / materials for active and passive equipment, 24 ports switch. The data cabinet shall be complete in all respects including cost of all necessary materials / accessories required for proper functioning for the data cabinet. Data cabinet shall be installed after obtaining necessary permission from the computer specialist of the Client. | Each | 1 |  |  | 0
| 15-136-h | Supply, Installation, testing and commissioning of 42 port DATA cabinet with 3 no’s cabinet tray, 4 no’s power socket and with flexi glass door | Each | 1 |  |  | 0
| 15-138-f | Supply, Installation, testing and commissioning of Patch Cord CAT-6, 1m for computer complete in all respects | Each | 23 |  |  | 0
A.22 |  | Earthing System
| 15-105-h | Providing & fixing of Plate type Earthing commpressed with execveted hole 6"up 63 feet,GI pipe 2"(50mm)with Tees , Sockets , Endcap of 60 (Mtr) Copper Plate of 1/2"x 2"x 48", 2x 70mmsq S/Core copper bare conductor 125 (Mtr) Earth Connection Point of 200 x 50 x 50mm (L x W x T) Inspection Pit of 300 x 300 x 450 mm (L x W x D) complated with all respect | Each | 4 |  |  | 0
| 15-105-i | Construction of water tight brick type Grounding inspection pit. | Each | 4 |  |  | 0
B.01 |  | Switch & Sockets.
i | Appendix ' c' Page No-1 | Supply and installation of Floor Box / Technology Box, Suiteable for 1 No. Telephone outlet and 1 no. Data outlet, including cost of 2 No. 10/13 Amp socket and 1 no. 5 Amp Socket. | Each | 35 |  |  | 0
B.02 |  | 5-KVA Online UPS Un-Intruptible Power Supply for Main Data / Server Cabinet.
| Appendix ' c' Page No-2 | Supply at Site, Installation of Online5 KVA UPS with 0.8 Power Factor with dry gel battries for standard backup upto 15 minutes. Make : APC, I-Power - Emerson. | Each | 2 |  |  | 0
B.03 |  | WIFI ACCESS POINT
| Appendix ' c' Page No-3 | Supply, installation and connections of wireless wave two Wi-Fi access point or equivalent 2533Mbps dual-band, 802.11 abgn/ac with 20,40,80 MHz Channel width Support 4x4:4 streams, Beam Flex, Dual Polarized Integrated smart Directional antenna array. Auto-sensing 10/100/1000 Mbps, RJ-45 Power over Ethernet (PoE) Integrated 24 Antenna elements with more than 3000 Antenna Patterns, 15db interference mitigation, make Ruckus, Aruba, Linksys or as specified in appendix-A as approved by engineer's Incharge or consultants, Actual quantities shall be measured as per site & paid accordingly. Complete in all respects | Each | 1 |  |  | 0
Server Machine
| Appendix ' c' Page No-4 | Supply at site, 2 x Intel Xeon E5-2630 v4 2.2GHz, 25 M cache, 8.0 GT/s, QPI, Turbo, HT, 10C/20T(85W)85W, Chipset: Genuine Intel, Memory: 32GB(2x16GB) RDIMM, multi Slots, Storage: 3 x 1TB 7.2k RPM Near Line SAS 12 Gbps, Drive bays: 2.5” Drive, Raid Controller: RAID 5 for H330/H730P/H730, Network: Dual Port Ethernet, DVD +/- RW, Display: 18.5” LCD, Power Supply: 2 x power cord 12A 4M C13/C14, hot plug, Redundant, Ready Rail Sloiding Rails with Cable Management arm, Chasis: 2U, Windows Server 2012, Warranty : 03 Years | Each | 1 |  |  | 0
B.04 |  | MONITOR
| Appendix ' c' Page No-5 | Supply, installation and connections of 32" BACKLIT LED 1080p monitor with operation capacity of 24/7 wit 3 year warranty. make by Samsung, TCL, LG or as specified in appendix-A approved equivalent by consultant or Engineer Incharge, Complete in all respectsActual quantities shall be measured as per site & paid accordingly. Complete in all respects. | Nos. | 1 |  |  | 0
B.05 |  | Non-maintained Emergency Lighting | [5 empty] | 0
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 12 |  |  | 0
B.06 |  | 2-KVA Online UPS Un-Intruptible Power Supply for Building | [5 empty] | 0
| Appendix ' c' Page No-2 | Supply at Site, Installation of Online 02 KVA UPS with 0.8 Power Factor with dry gel battries for standard backup upto 60 minutes including cost of rack complete by all respect as approved by engineer incharge. Make : APC,Delpro(uk) - Emerson. | Each | 2 |  |  | 0
SUB TOTAL ELECTRICAL WORKS | [6 empty] | 0

## 11-Plumb (AB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 11: ADMIN BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
PLUMBING WORKS
Indian W.C
1 | 14-03-a | Providing and fitting glazed earthenware water closet (WC), squatter type (orisa pattern) combined with foot rest. complete in all respects : White | Each | 1 |  |  | 0
WC European
2 | 14-01-a | Providing and Fixing glazed earthen ware WC European type of approved size excluding cost of seat & cover, complete in all respects: White | Each | 3 |  |  | 0
3 | 14-10-a | Providing and Fixing glazed earthen ware low down flushing cistern 3 gallons (13.63 Liters) capacity including bracket set, copper connection,etc. complete in all respects: White | Each | 4 |  |  | 0
4 | 14-05-a-01 | Providing and Fixing glazed earthen ware wash hand basin (WHB) complete size 56x40 cm (22"x16"), including bracket set, waste coupling, complete in all respects: White with pedestal (Best Quality) | Each | 4 |  |  | 0
5 | 14-102 | Providing & Fixing of SHOWER SET locally made complete with concealed T-STOP COCK for cold and hot water supply with mixer, swivel shower rose, long bib cock etc Complete in all respect. | Each | 4 |  |  | 0
6 | 14-27-a | Providing and fixing chorimum plated (CP) mixing valve for wash hand basin (WHB), sink or shower of approved (Best) quality | Each | 12 |  |  | 0
7 | 14-06-a | Providing and Fixing stainless steel sink with drain board size (120 x 60 cm) 48"x24", including set of brackets, waste pipe etc - (Best Quality) | Each | 1 |  |  | 0
8 | 14-13 | Providing and fixing choricum plated soap dish complete. | Each | 4 |  |  | 0
9 | 14-16-a | Providing and Fixing chromium plated (CP) towel 60 cm (24") long and 2 cm (3/4") dia | Each | 4 |  |  | 0
10 | 14-17-a | Providing and fixing best quality looking glass 5 mm thick neatly fitted on masonry wall etc. as per instruction of Engineer In-charge complete. Mirror 60 x 45 cm (24"x18") size | Each | 4 |  |  | 0
11 | 14-21-c | Providing and fixing chromium plated (CP) double bib cock, heavy duty of approved quality : 1.5 cm (1/2") | Each | 4 |  |  | 0
12 | 14-25-a | Providing and fixing chromium plated (CP) tee stop cock 1.5 cm (1/2") of approved quality | Each | 12 |  |  | 0
13 | 14-31-a | Providing and Fixing cast iron (CI) floor trap of approved quality including CI grating & concrete chamber all round : 4"x2" (100mm x 50 mm) | Each | 12 |  |  | 0
14 | 14-33 | Providing and Fixing 4" gully trap of approved quality including cement concrete cost of PVC grating 6" x6" (150 x 150 mm) and masonry chamber 12"x12" (300 x 300 mm). | Each | 4 |  |  | 0
15 | 14-157 | P-Trap (uPVC) for squatting type WC.
| 14-157 | ii) 10 cm (4") glazed. | Each | 4 |  |  | 0
SEWERAGE SYSTEM
16 | 14-95-a | Making connection with the existing system PVC pipe line including cutting the pipe for providing & fixing required fittings : Class B PVC
|  | a) 3" i/d (75 mm) | M | 40 |  |  | 0
|  | b) 4" i/d (100 mm) | M | 25 |  |  | 0
|  | d) 6" i/d (150 mm) | M | 30 |  |  | 0
1 | NS-1 | Providing, fixing, jointing and testing Polypropylene Random (PPR) PN20 pressure pipe for cold, hot and hot water return water as per DIN 8077-8078 for pipes and DIN 16962,PN25 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, walls cutting for pipelines, complete in all respect as per specifications and drawings as well as directed by the Engineer.
|  | 20 mm dia | M | 40 |  |  | 0
|  | 25 mm dia | M | 20 |  |  | 0
|  | 32 mm dia | M | 35 |  |  | 0
2 | NS-2 | Providing and making Manhole 2'x2' internal size including 9" thick brick masonry (1:4), 1/2" th. Plastering (1:3) i/side, benching with PCC 1:2:4 4" th. with cement finish, excluding manhole cover, complete in all respects. | Each | 2 |  |  | 0
3 | NS-3 | Providing and fixing food grade plastic over head water tank (200 gallon) including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Each | 1 |  |  | 0
SUB TOTAL OF PLUMBING WORKS | [6 empty] | 0

## 12-Summary(chem B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 12: CHEMICAL BUILDING
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 12-Civil (Chem B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 12: CHEMICAL BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-25-d | Excavation in foundation of building, bridges etc complete : in shingle/gravel | M3 | 900.11 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 270.03 |  |  | 0
Anti-Termite
2 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 2751.69 |  |  | 0
Plain and Reinforement Concrete
3 | 06-05-i | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:4:8) | M3 | 356.44 |  |  | 0
FOUNDATION
4 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 468.14 |  |  | 0
GROUND FLOOR
5 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 111.96 |  |  | 0
6 | 06-07-a-02 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1.5:3) | M3 | 170.4 |  |  | 0
FIRST FLOOR
7 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 5.07 |  |  | 0
8 | 06-07-a-02 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1.5:3) | M3 | 136.73 |  |  | 0
Steel Reinforcement
9 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 210.15 |  |  | 0
10 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 26.88 |  |  | 0
11 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 35.28 |  |  | 0
Brick Work
12 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 50.09 |  |  | 0
GROUND FLOOR
13 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 115.64 |  |  | 0
FIRST FLOOR
14 | 07-05-a-04 | 1st class brick work in first floor Cement, sand mortar 1:5 | M3 | 22.59 |  |  | 0
Flooring
15 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 2478.32 |  |  | 0
16 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 3.21 |  |  | 0
17 | 10-22-b | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 135.66 |  |  | 0
18 | 10-41-b-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 20.67 |  |  | 0
Surface Rendring
19 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 945 |  |  | 0
20 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 695.15 |  |  | 0
21 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 (External walls) | M2 | 560.18 |  |  | 0
22 | 11-18-b | Cement pointing struck joints, on walls, upto 30' height : Ratio 1:3 (External walls) | M2 | 425.83 |  |  | 0
Painting and Warnishing
23 | 11-20-a | Priming coat of chalk under distemper | M2 | 1722.16 |  |  | 0
24 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 1722.16 |  |  | 0
25 | 13-25-a+(bx2) | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 1014.01 |  |  | 0
26 | 13-03-c-01+(c-02x2) | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 10.58 |  |  | 0
Metal Work
27 | 12-57-b | Providing and fixing double leaf steel door with frame fully panelled with M.S sheet 16 gauge (1.59mm) painted with two coats of red oxide paint with brass fitting of approved make including cost of fabrication, iron lugs, cutting holes and making good the damages to walls. | M2 | 5.29 |  |  | 0
28 | 25-39-a-01 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 34.02 |  |  | 0
29 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 40.82 |  |  | 0
30 | 25-10 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Louvre Gate including duly painting red oxide) | Tonne | 0.15 |  |  | 0
Roofing & Water Proofing
31 | 9-06+13 + 6- 28 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 945 |  |  | 0
32 | 09-16 | Khuras on roof 2'x2'x6" | Each | 5 |  |  | 0
33 | 9-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 5 |  |  | 0
34 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 270.03 |  |  | 0
35 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 270.03 |  |  | 0
36 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 270.03 |  |  | 0
37 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 270.03 |  |  | 0
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 11.52 |  |  | 0
Miscellenious
2 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:4" dia | M | 1.75 |  |  | 0
3 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:4" dia | Each | 5 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 12-Mechanical (Chem B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 12: CHEMICAL BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Top-Running Double-Girder Bridge Cranes
Providing, installing, testing and commissioning Top-Running Double-Girder Bridge Cranes, of internationally reputed approved make, complete with all its moving components, drives, drive controls, safety mechanisms, cables, cables collapsing mechanisms, operation-control equipment, and side rails, to be supported on the structure, including all jointing, fixing & installation accessories, initial charging of lubricants, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Chemical Building: Capacity: 5 Tons | Each | 1 |  |  | 0
2 | NS-2 | MIXER
Providing, installing, testing and commissioning Mechanical Mixers (vertical-shaft, single impeller, pitched blade or propeller type, 3-4 blades), of internationally reputed approved make, complete with motor (4 pole, installed power to be determined by the manufacturer), gear box, motor starter, support base/frame, shaft, impeller and canopy, with all the submerged/wetted components to be of stainless steel (Grade 316), including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Alum Dosing Tanks (Imparted Mixing Power: 2.9 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 0.9 – 1.2 m) | Each | 2 |  |  | 0
|  | In Lime Dosing Tanks (Imparted Mixing Power: 2.9 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 0.9 – 1.2 m) | Each | 2 |  |  | 0
|  | In Polymer 1 Dosing Tanks (Imparted Mixing Power: 2.9 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 0.9 – 1.2 m) | Each | 2 |  |  | 0
3 | NS-3 | Stock Solution Transfer Pumps
Providing, installing, testing and commissioning Alum Water Transfer Pumps (horizontal-shaft, end-suction, non-clogging/solids-handling, centrifugal type, Min Free Passage Size: 100 mm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Min Efficiency 90%), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Alum Stock Solution Transfer pump: Capacity: 20m3/hr, Head:3m | Each | 2 |  |  | 0
|  | Lime Stock Solution Transfer pump: Capacity: 20m3/hr, Head:3m | Each | 2 |  |  | 0
|  | Polymer Stock Solution Transfer pump: Capacity: 20m3/hr, Head:3m | Each | 2 |  |  | 0
4 | NS-4 | Dosing Pumps
Providing, installing, testing and commissioning Alum Dosing Pumps (horizontal-diaphragm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Min Efficiency 90%), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Alum Dosing Pump; Capacity: 1.2m3/hr, Head: 40ft | Each | 5 |  |  | 0
|  | Lime Dosing Pump; Capacity: 1.2m3/hr, Head: 40ft | Each | 5 |  |  | 0
|  | Polymer Dosing Pump; Capacity: 1.2m3/hr, Head: 40ft | Each | 5 |  |  | 0
5 | NS-5 | Sluice Valves
Providing, installing and testing cast iron (CI) Sluice Valves (Swing type, Flanged, BS 5153, PN 10) on pipelines, of internationally reputed approved make, including gaskets, steel nuts & bolts and other jointing accessories, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows:
|  | 32mm | Each | 54 |  |  | 0
6 | NS_6 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 32mm ( including fittings as Bends etc) | M | 158 |  |  | 0
7 | NS-7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10, 90mm ( including fittings as Bends etc) | M | 34 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 12-ELECTRICAL (Chem B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 12: CHEMICAL BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 170.73 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 42.68 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 676.83 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 225.61 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 768.29 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 256.1 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 5 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 12 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 137.2 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 45.73 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 493.9 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 164.63 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 201.22 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 67.07 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 548.78 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 182.93 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 182.93 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 30 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 548.78 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 182.93 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 182.93 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 30 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 36.59 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 6 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 100 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 10 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 36 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | Nos. | 36 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.34 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6 |  |  | 0
A.16 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 13-Summary (Cl2 B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 13: CHLORINATION BUILDING
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 13-Civil (Cl B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 13: CHLORINATION BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-25-d | Excavation in foundation of building, bridges etc complete : in shingle/gravel | M3 | 259.15 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 77.75 |  |  | 0
Anti-Termite
3 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 821.59 |  |  | 0
Plain and Reinforement Concrete
4 | 06-05-i | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:4:8) | M3 | 71.56 |  |  | 0
FOUNDATION
5 | 06-07-a-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 155.67 |  |  | 0
GROUND FLOOR
6 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 51.22 |  |  | 0
7 | 06-07-a-02 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1.5:3) | M3 | 28.87 |  |  | 0
FIRST FLOOR
8 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 4.89 |  |  | 0
9 | 06-07-a-02 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1.5:3) | M3 | 56.28 |  |  | 0
Steel Reinforcement
10 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 69.93 |  |  | 0
11 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 13.15 |  |  | 0
12 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 34.52 |  |  | 0
Brick Work
13 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 28.22 |  |  | 0
GROUND FLOOR
14 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 63.87 |  |  | 0
FIRST FLOOR
15 | 07-05-a-04 | 1st class brick work in first floor Cement, sand mortar 1:5 | M3 | 16.31 |  |  | 0
Flooring
16 | 07-10 | Supplying and filling sand under floor or plugging in wells | M3 | 535.77 |  |  | 0
17 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 2.14 |  |  | 0
18 | 10-22-b | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 63 |  |  | 0
19 | 10-41-b-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 9.6 |  |  | 0
Surface Rendring
20 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 192.22 |  |  | 0
21 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 402.78 |  |  | 0
22 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 (External walls) | M2 | 316.47 |  |  | 0
23 | 11-18-b | Cement pointing struck joints, on walls, upto 30' height : Ratio 1:3 (External walls) | M2 | 84.61 |  |  | 0
Painting and Warnishing
24 | 11-20-a | Priming coat of chalk under distemper | M2 | 624.75 |  |  | 0
25 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 624.75 |  |  | 0
26 | 13-25-a+(bx2) | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 416.9 |  |  | 0
27 | 13-03-c-01+(c-02x2) | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 10.58 |  |  | 0
|  | Metal Work |  |  |  |  | 0
28 | 12-57-b | Providing and fixing double leaf steel door with frame fully panelled with M.S sheet 16 gauge (1.59mm) painted with two coats of red oxide paint with brass fitting of approved make including cost of fabrication, iron lugs, cutting holes and making good the damages to walls. | M2 | 5.29 |  |  | 0
29 | 25-39-a-01 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 13.61 |  |  | 0
30 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 27.22 |  |  | 0
31 | 25-10 | Fabrication of heavy steel work with angle, tees, sheet iron etc for making trusses, girders etc including Erection and fitting in position iron trusses, staging of water tanks, etc (for Louvre Gate including duly painting red oxide) | Tonne | 0.15 |  |  | 0
Roofing & Water Proofing
32 | 9-06+13 + 6- 28 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 201.6 |  |  | 0
33 | 09-16 | Khuras on roof 2'x2'x6" | Each | 2 |  |  | 0
34 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 2 |  |  | 0
35 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 77.75 |  |  | 0
36 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 77.75 |  |  | 0
37 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 77.75 |  |  | 0
| 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 77.75 |  |  | 0
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 4.61 |  |  | 0
Miscellenious
2 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:4" dia | M | 0.7 |  |  | 0
3 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:4" dia | Each | 2 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 13-Mechanical (Cl B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 13: CHLORINATION BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Top-Running Double-Girder Bridge Cranes
Providing, installing, testing and commissioning Top-Running Double-Girder Bridge Cranes, of internationally reputed approved make, complete with all its moving components, drives, drive controls, safety mechanisms, cables, cables collapsing mechanisms, operation-control equipment, and side rails, to be supported on the structure, including all jointing, fixing & installation accessories, initial charging of lubricants, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Chlorine Building: Capacity: 5 Tons | Each | 1 |  |  | 0
2 | NS-2 | MIXER
Providing, installing, testing and commissioning Mechanical Mixers (vertical-shaft, single impeller, pitched blade or propeller type, 3-4 blades), of internationally reputed approved make, complete with motor (4 pole, installed power to be determined by the manufacturer), gear box, motor starter, support base/frame, shaft, impeller and canopy, with all the submerged/wetted components to be of stainless steel (Grade 316), including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In Sodium Hypochlorite Dosing Tank (Imparted Mixing Power: 0.45 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 0.6 – 0.8 m) | Each | 2 |  |  | 0
|  | In polymer 2 Dosing Tank (Imparted Mixing Power: 0.45 kW, Rotational Speed: 40 – 100 RPM, Impeller Diameter: 0.6 – 0.8 m) | Each | 2 |  |  | 0
1 |  | Stock SolutionTransfer Pumps
Providing, installing, testing and commissioning Sodium Hypochlorite Water Transfer Pumps (horizontal-shaft, end-suction, non-clogging/solids-handling, centrifugal type, Min Free Passage Size: 100 mm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Min Efficiency 90%), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows
|  | NaOCL Stock Solution Transfer pump: Capacity: 10m3/hr, Head:3m | Each | 2 |  |  | 0
|  | Polymer Stock Solution Transfer pump: Capacity: 10m3/hr, Head:3m | Each | 2 |  |  | 0
2 |  | Sodium Hypochlorite Dosing Pumps
Providing, installing, testing and commissioning Sodium Hypochlorite Dosing Pumps (horizontal-diaphragm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Min Efficiency 90%), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | NaOCl Dosing Pump; Capacity: 0.2m3/hr, Head: 40ft | Each | 3 |  |  | 0
|  | Polymer Dosing Pump; Capacity: 0.2m3/hr, Head: 40ft | Each | 3 |  |  | 0
6 | NS-6 | Sluice Valves
Providing, installing and testing cast iron (CI) Sluice Valves (Swing type, Flanged, BS 5153, PN 10) on pipelines, of internationally reputed approved make, including gaskets, steel nuts & bolts and other jointing accessories, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows:
|  | 32mm | Each | 20 |  |  | 0
7 | NS-7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 32mm ( including fittings as Bends etc) | M | 48 |  |  | 0
8 | NS-8 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 90mm ( including fittings as Bends etc) | M | 26 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 13-Electrical (Cl2 B)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 13: CHLORINATION BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 170.73 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 42.68 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 567.07 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 189.02 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 414.63 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 138.21 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 6 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 12 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 109.76 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 36.59 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 182.93 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 60.98 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 548.78 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 182.93 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 182.93 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 30 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 548.78 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 182.93 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 182.93 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 30 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 36.59 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 6 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 43 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | Nos. | 22 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 8 |  |  | 0
| 26-01-l-01 | Supply and Erection of ACEnergy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 8 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" Wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.34 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6
A.15 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 14-Summery (SSB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 14: SUB-STATION BUILDING
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
TOTAL AMOUNT |  | 0

## 14-CIVIL (SSB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 14: SUB-STATION BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Excavation in foundation of building, bridges etc complete : in shingle/gravel | M3 | 59.95 |  |  | 0
2 | 03-67-b-ii | Structural Excavation In Medium Rock Material | M3 | 179.85 |  |  | 0
3 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | M3 | 159.86 |  |  | 0
4 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 8 km. (as per actual borrow pit lead) | M3 | 239.79 |  |  | 0
Anti-Termite
5 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 326.81 |  |  | 0
Plain and Reinforement Concrete
6 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 9.18 |  |  | 0
GROUND FLOOR
| 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 25.92 |  |  | 0
7 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 69.54 |  |  | 0
Steel Reinforcement
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 22.39 |  |  | 0
9 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 12.8 |  |  | 0
10 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 12.8 |  |  | 0
Brick Work
11 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 24.32 |  |  | 0
GROUND FLOOR
12 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 27.24 |  |  | 0
Flooring
13 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 8.85 |  |  | 0
14 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 8.85 |  |  | 0
15 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 4.41 |  |  | 0
16 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 89.29 |  |  | 0
17 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 6.2 |  |  | 0
Surface Rendring
18 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 88.2 |  |  | 0
19 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 166.32 |  |  | 0
20 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 137.74 |  |  | 0
Painting and Warnishing
21 | 11-20-a | Priming coat of chalk under distemper | M2 | 267.25 |  |  | 0
22 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 267.25 |  |  | 0
23 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 144.63 |  |  | 0
24 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 32.77 |  |  | 0
Metal Work
25 | 12-57-a | Providing and fixing single leaf steel door with frame fully panelled with M.S sheet 16 gauge (1.59mm) painted with two coats of red oxide paint with brass fitting of approved make including cost of fabrication, iron lugs, cutting holes and making good the damages to walls. | M2 | 8.7 |  |  | 0
26 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 7.68 |  |  | 0
27 | 12-66 | Supply and Fixing of double glazed aluminium (color as approved) Premium model (Gauge 2 mm) 4" sect. Sliding window, including all necessary fittngs and fly screen shutters complete. | M2 | 10.75 |  |  | 0
28 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | M2 | 10.75 |  |  | 0
29 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | M | 4.2 |  |  | 0
Roofing & Water Proofing
30 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 80.85 |  |  | 0
31 | 09-16 | Khuras on roof 2'x2'x6" | Each | 2 |  |  | 0
32 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 2 |  |  | 0
33 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 159.86 |  |  | 0
34 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 159.86 |  |  | 0
35 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 159.86 |  |  | 0
36 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 159.86 |  |  | 0
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 1.92 |  |  | 0
Miscellenious
2 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 9.6 |  |  | 0
3 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 2 |  |  | 0
4 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 2 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 14-ELECTRICAL (SSB)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 14: SUB-STATION BUILDING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.7805 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.1951 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 73.1707 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 24.3902 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.1463 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.7154 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.878 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.2927 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.878 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.2927 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.5854 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.1951 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 54.878 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 18.2927 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 18.2927 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 5 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 91.4634 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 30.4878 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 30.4878 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 5 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.5854 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.1951 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.1951 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 9 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | Nos. | 4 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" Wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.3415 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6 |  |  | 0
A.16 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 15-Summery (ECR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 15: ELECTRICAL CONTROL ROOM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 15-CIVIL (ECR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 15: ELECTRICAL CONTROL ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation in Common Material bymechanical means | M3 | 239.79 |  |  | 0
2 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | M3 | 159.86 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 8 km. (as per actual borrow pit lead) | M3 | 176.25 |  |  | 0
Anti-Termite
4 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 497.51 |  |  | 0
Plain and Reinforement Concrete
5 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 9.18 |  |  | 0
GROUND FLOOR
6 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 25.92 |  |  | 0
7 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 47.59 |  |  | 0
Steel Reinforcement
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 17.09 |  |  | 0
9 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 9.6 |  |  | 0
10 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 25.6 |  |  | 0
Brick Work
11 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 15.8 |  |  | 0
GROUND FLOOR
12 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 27.24 |  |  | 0
Flooring
13 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 10.34 |  |  | 0
14 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 10.34 |  |  | 0
15 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 5.15 |  |  | 0
16 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 101.85 |  |  | 0
17 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 6.63 |  |  | 0
Surface Rendring
18 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 95.55 |  |  | 0
19 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 307.22 |  |  | 0
20 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 159.5 |  |  | 0
Painting and Warnishing
21 | 11-20-a | Priming coat of chalk under distemper | M2 | 422.91 |  |  | 0
22 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 422.91 |  |  | 0
23 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 167.48 |  |  | 0
24 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 15.36 |  |  | 0
Metal Work
25 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 7.68 |  |  | 0
26 | 12-66 | Supply and Fixing of double glazed aluminium (color as approved) Premium model (Gauge 2 mm) 4" sect. Sliding window, including all necessary fittngs and fly screen shutters complete. | M2 | 13.83 |  |  | 0
27 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | M2 | 13.83 |  |  | 0
28 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | M | 4.2 |  |  | 0
Roofing & Water Proofing
29 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 95.55 |  |  | 0
30 | 09-16 | Khuras on roof 2'x2'x6" | Each | 2 |  |  | 0
31 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 2 |  |  | 0
31 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 159.86 |  |  | 0
32 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 159.86 |  |  | 0
33 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 159.86 |  |  | 0
33 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 159.86 |  |  | 0
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 2.3 |  |  | 0
Miscellenious
2 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 9.6 |  |  | 0
3 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 2 |  |  | 0
4 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 2 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 15-Electrical (ECR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 15: ELECTRICAL CONTROL ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.78 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 128.05 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 42.68 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.15 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.72 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 6 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 36.59 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 6 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 12 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 4 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.34 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting | [5 empty] | 0
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6 |  |  | 0
A.16 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
Sub Total of Electrical Works | [6 empty] | 0

## 16-Summery (GR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 16: GENERATOR ROOM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 16-CIVIL (GR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 16: GENERATOR ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation in Common Material bymechanical means | M3 | 239.79 |  |  | 0
3 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | M3 | 159.86 |  |  | 0
Anti-Termite
4 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 326.81 |  |  | 0
5 |  | Plain and Reinforement Concrete
6 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 9.18 |  |  | 0
GROUND FLOOR
7 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 25.92 |  |  | 0
8 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 75.93 |  |  | 0
Steel Reinforcement
9 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 22.54 |  |  | 0
10 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 12.8 |  |  | 0
11 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 12.8 |  |  | 0
Brick Work
12 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 22.48 |  |  | 0
13 |  | GROUND FLOOR
14 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 27.24 |  |  | 0
Flooring
15 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 10.34 |  |  | 0
16 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 10.34 |  |  | 0
17 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 5.15 |  |  | 0
18 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 103.99 |  |  | 0
19 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 6.63 |  |  | 0
Surface Rendring
20 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 95.55 |  |  | 0
21 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 166.32 |  |  | 0
22 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 151.44 |  |  | 0
Painting and Warnishing
23 | 11-20-a | Priming coat of chalk under distemper | M2 | 274.96 |  |  | 0
24 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 274.96 |  |  | 0
25 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 159.01 |  |  | 0
26 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 32.77 |  |  | 0
Metal Work
27 | 12-57-a | Providing and fixing single leaf steel door with frame fully panelled with M.S sheet 16 gauge (1.59mm) painted with two coats of red oxide paint with brass fitting of approved make including cost of fabrication, iron lugs, cutting holes and making good the damages to walls. | M2 | 8.7 |  |  | 0
28 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 7.68 |  |  | 0
29 | 12-66 | Supply and Fixing of double glazed aluminium (color as approved) Premium model (Gauge 2 mm) 4" sect. Sliding window, including all necessary fittngs and fly screen shutters complete. | M2 | 10.75 |  |  | 0
30 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | M2 | 10.75 |  |  | 0
31 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | M | 4.2 |  |  | 0
Roofing & Water Proofing
32 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 95.55 |  |  | 0
33 | 09-16 | Khuras on roof 2'x2'x6" | Each | 2 |  |  | 0
34 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 2 |  |  | 0
35 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 37.16 |  |  | 0
36 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 37.16 |  |  | 0
37 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 37.16 |  |  | 0
38 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 37.16 |  |  | 0
NON SCHEDULE ITEMS-B
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 1.92 |  |  | 0
Miscellenious
2 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 9.6 |  |  | 0
3 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 2 |  |  | 0
4 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 2 |  |  | 0
SUB TOTAL OF CIVIL WORK | [6 empty] | 0

## 16-Electrical (GR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 16: GENERATOR ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.78 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 128.05 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 42.68 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.15 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.72 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 6 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 36.59 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 6 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 12 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 4 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.34 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 6 |  |  | 0
A.16 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects. : 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 17-Summery (Guard R)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 17: GUARD ROOM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
3 | PLUMBING WORKS | 0
TOTAL AMOUNT |  | 0

## 17-CIVIL (Guard R)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 17: GUARD ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation in Common Material bymechanical means | M3 | 37.74 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 25.16 |  |  | 0
Anti-Termite
3 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 162.28 |  |  | 0
Plain and Reinforement Concrete
4 | 06-03-b | Cement Concrete (brick/stone ballast, 1.5" to 2"/nullah shingle well graded and cleaned) in foundation & plinth (Ratio 1:4:8) | M3 | 5.85 |  |  | 0
GROUND FLOOR
5 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 12.29 |  |  | 0
Steel Reinforcement
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 1.01 |  |  | 0
7 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 15.6 |  |  | 0
8 | 06-26-a-02 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 24.26 |  |  | 0
Brick Work
9 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 30.45 |  |  | 0
GROUND FLOOR
10 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 27.49 |  |  | 0
Flooring
11 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 7.43 |  |  | 0
12 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 7.43 |  |  | 0
13 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 3.7 |  |  | 0
14 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 65.26 |  |  | 0
15 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 8.94 |  |  | 0
16 | 10-51 | Providing and Fixing of Ceramic Tiles 12"×24" of Imported Approved Quality with jointing and finishing | M2 | 7.91 |  |  | 0
Surface Rendring
17 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 60.66 |  |  | 0
18 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 172.58 |  |  | 0
19 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 117.61 |  |  | 0
Wood Work
20 | 12-56-b | Providing and fixing 1.5" (38 mm) thick pressed veneered door shutters fully flushed with First class wood veneering on all faces and sides fixed over partal wood cavited core and frame work of not less than 4" (100mm) wide strips all round with approved iron hinges, tower bolts as required. | M2 | 8.18 |  |  | 0
21 | 12-70-a | Supply and Fixing MS Sheet 16 guage(10'' x 2'') box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc | M2 | 20.7 |  |  | 0
22 | 12-24-a-02 | providing/fixing approved quality Rim locks : Imported | Each | 4 |  |  | 0
23 | 12-22-a-01 | Providing and fixing sliding bolt to doors Iron sliding bolts : 10" long | Each | 3 |  |  | 0
24 | 12-78-a | Kitchen Floor Cabinet as per MES Design/Specification. | M2 | 1.52 |  |  | 0
25 | 12-78-b | Kitchen Wall Cabinet as per MES Design/Specification. | M2 | 1.1 |  |  | 0
Painting and Warnishing
26 | 11-20-a | Priming coat of chalk under distemper | M2 | 244.91 |  |  | 0
27 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 244.91 |  |  | 0
28 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 123.49 |  |  | 0
29 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 16.35 |  |  | 0
Metal Work
30 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 7.68 |  |  | 0
Roofing & Water Proofing
31 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 73.9 |  |  | 0
32 | 09-16 | Khuras on roof 2'x2'x6" | Each | 1 |  |  | 0
33 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 1 |  |  | 0
34 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 25.16 |  |  | 0
35 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 25.16 |  |  | 0
36 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 25.16 |  |  | 0
37 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 25.16 |  |  | 0
NON SCHEDULE ITEMS-B
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 2.08 |  |  | 0
2 | N.S | Providing and laying Pre-polished Black Granite one-piece marble slabs Kitchen / Vanity Counter etc; laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment, making rounding edge and chemical polishing etc; complete in all respect, as per drawings and Specifications, sample as approved by The Engineer. | M2 | 1.1 |  |  | 0
Miscellenious
3 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 9.6 |  |  | 0
4 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 1 |  |  | 0
5 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 1 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 17-Electrical (Guard R)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 17: GUARD ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 73.17 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 18.29 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 128.05 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 42.68 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.15 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.72 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 27.44 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 9.15 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 41.16 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 13.72 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 54.88 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 18.29 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 7 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 128.05 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 42.68 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 42.68 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 7 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | Nos. | 6 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 12 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 4 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 2 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 2 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC ENERGY EFFICIENT CEILING FANS 56 inch, 50 W | Nos. | 2 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | Nos. | 1 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | M | 9.15 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
A.17 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 1 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 17-Plumb(GR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 17: GUARD ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
PLUMBING WORKS
Indian W.C
1 | 14-03-a | Providing and fitting glazed earthenware water closet (WC), squatter type (orisa pattern) combined with foot rest. complete in all respects : White | Each | 1 |  |  | 0
2 | 14-10-a | Providing and Fixing glazed earthen ware low down flushing cistern 3 gallons (13.63 Liters) capacity including bracket set, copper connection,etc. complete in all respects: White | Each | 1 |  |  | 0
3 | 14-05-a-01 | Providing and Fixing glazed earthen ware wash hand basin (WHB) complete size 56x40 cm (22"x16"), including bracket set, waste coupling, complete in all respects: White with pedestal (Best Quality) | Each | 1 |  |  | 0
4 | 14-102 | Providing & Fixing of SHOWER SET locally made complete with concealed T-STOP COCK for cold and hot water supply with mixer, swivel shower rose, long bib cock etc Complete in all respect. | Each | 1 |  |  | 0
5 | 14-27-a | Providing and fixing chorimum plated (CP) mixing valve for wash hand basin (WHB), sink or shower of approved (Best) quality | Each | 3 |  |  | 0
6 | 14-06-a | Providing and Fixing stainless steel sink with drain board size (120 x 60 cm) 48"x24", including set of brackets, waste pipe etc - (Best Quality) | Each | 1 |  |  | 0
7 | 14-13 | Providing and fixing choricum plated soap dish complete. | Each | 2 |  |  | 0
8 | 14-16-a | Providing and Fixing chromium plated (CP) towel 60 cm (24") long and 2 cm (3/4") dia | Each | 2 |  |  | 0
9 | 14-17-a | Providing and fixing best quality looking glass 5 mm thick neatly fitted on masonry wall etc. as per instruction of Engineer In-charge complete. Mirror 60 x 45 cm (24"x18") size | Each | 1 |  |  | 0
10 | 14-21-c | Providing and fixing chromium plated (CP) double bib cock, heavy duty of approved quality : 1.5 cm (1/2") | Each | 1 |  |  | 0
11 | 14-25-a | Providing and fixing chromium plated (CP) tee stop cock 1.5 cm (1/2") of approved quality | Each | 3 |  |  | 0
12 | 14-31-a | Providing and Fixing cast iron (CI) floor trap of approved quality including CI grating & concrete chamber all round : 4"x2" (100mm x 50 mm) | Each | 3 |  |  | 0
13 | 14-33 | Providing and Fixing 4" gully trap of approved quality including cement concrete cost of PVC grating 6" x6" (150 x 150 mm) and masonry chamber 12"x12" (300 x 300 mm). | Each | 1 |  |  | 0
14 | 14-157 | P-Trap (uPVC) for squatting type WC.
| 14-157 | ii) 10 cm (4") glazed. | Each | 1 |  |  | 0
SEWERAGE SYSTEM
15 | 14-95-a | Making connection with the existing system PVC pipe line including cutting the pipe for providing & fixing required fittings : Class B PVC
|  | a) 3" i/d (75 mm) | m | 20 |  |  | 0
|  | b) 4" i/d (100 mm) | m | 20 |  |  | 0
|  | d) 6" i/d (150 mm) | m | 20 |  |  | 0
NON-SCHEDULE ITEM
1 | NS-1 | Providing, fixing, jointing and testing Polypropylene Random (PPR) PN20 pressure pipe for cold, hot and hot water return water as per DIN 8077-8078 for pipes and DIN 16962,PN25 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, walls cutting for pipelines, complete in all respect as per specifications and drawings as well as directed by the Engineer.
|  | 20 mm dia | m | 25 |  |  | 0
|  | 25 mm dia | m | 20 |  |  | 0
|  | 32 mm dia | m | 20 |  |  | 0
2 | NS-2 | Providing and making Manhole 2'x2' internal size including 9" thick brick masonry (1:4), 1/2" th. Plastering (1:3) i/side, benching with PCC 1:2:4 4" th. with cement finish, excluding manhole cover, complete in all respects. | Each | 2 |  |  | 0
3 | NS-3 | Providing and fixing food grade plastic over head water tank (200 gallon) including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Each | 1 |  |  | 0
SUB TOTAL OF PLUMBING WORKS | [6 empty] | 0

## 18-Summary (WOrkshop)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 18: WORKSHOP
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 18-Civil (workshop)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 18: WORKSHOP
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation in Common Material by mechanical means | M3 | 85.02 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 56.68 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 8 km. (as per actual borrow pit lead) | M3 | 170.65 |  |  | 0
Anti-Termite
4 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 523.48 |  |  | 0
Plain and Reinforement Concrete
5 | 06-03-b | Cement Concrete (brick/stone ballast, 1.5" to 2"/nullah shingle well graded and cleaned) in foundation & plinth (Ratio 1:4:8) | M3 | 14.17 |  |  | 0
GROUND FLOOR
6 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 22.9 |  |  | 0
FIRST FLOOR
7 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 35.35 |  |  | 0
Steel Reinforcement
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 7.38 |  |  | 0
9 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 66.11 |  |  | 0
10 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 67.62 |  |  | 0
Brick Work
11 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 95.16 |  |  | 0
GROUND FLOOR
12 | 07-04-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 99.31 |  |  | 0
FIRST FLOOR
13 | 07-05-a-04 | 1st class brick work in first floor Cement, sand mortar 1:5 | M3 | 60.04 |  |  | 0
Flooring
14 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 19.16 |  |  | 0
15 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 19.16 |  |  | 0
16 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 9.55 |  |  | 0
17 | 10-55-g | Providing and Fixing of Porcelain Floor Tile 24" x 24" of approved quality | M2 | 21 |  |  | 0
18 | 10-51 | Providing and Fixing of Ceramic Tiles 12"×24" of Imported Approved Quality with jointing and finishing | M2 | 21 |  |  | 0
19 | 10-42 | Providing and fixing on walls1/4"(6mm approx.) thick of imported first grade ceramic tiles of size 24 in x 24 in of approved colour on walls, over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | M2 | 64.24 |  |  | 0
20 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 142.8 |  |  | 0
21 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 9.15 |  |  | 0
Surface Rendring
22 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 188.79 |  |  | 0
23 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 798.01 |  |  | 0
24 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 424.16 |  |  | 0
Wood Work
25 | 12-49-c | First class deodar wood wrought joinery in doors and windows etc. panelled or panelled or glazed or fully glazed fixed in position including chowkhat, holdfast, hinges, tower bolt rubber stop cleats/G I clamp, handles and chord with hooks etc. complete (excluding sliding bolts or lock) : 1½" (40mm) thick. | M2 | 2.35 |  |  | 0
26 | 12-56-b | Providing and fixing 1.5" (38 mm) thick pressed veneered door shutters fully flushed with First class wood veneering on all faces and sides fixed over partal wood cavited core and frame work of not less than 4" (100mm) wide strips all round with approved iron hinges, tower bolts as required. | M2 | 20.16 |  |  | 0
27 | 25-35 | Providing and Fixing 24 SWG GI sheet rolling shutter of steel frame of MS channel 2"x1.25"x1/8" complete | M2 | 19.2 |  |  | 0
28 | 12-70-a | Supply and Fixing MS Sheet 16 guage(10'' x 2'') box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc | M | 44.73 |  |  | 0
29 | 12-24-a-01 | providing/fixing approved quality Rim locks : Imported | Each | 8 |  |  | 0
30 | 12-22-a-01 | Providing and fixing sliding bolt to doors Iron sliding bolts : 10" long | Each | 3 |  |  | 0
31 | 12-21-b | P/F hydraulic Door Closer (Best Quality) | Each | 2 |  |  | 0
Painting and Warnishing
32 | 11-20-b | Providing and applying wall putty of 2mm thickness over plastered surface to prepare the surface even and smooth complete. | M2 | 1036.14 |  |  | 0
33 | 13-03-i | Providing and applying 3 coats of approved type of Plastic emulsion paint to Plastic surface as per manufucture specification. | M2 | 1036.14 |  |  | 0
34 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 445.37 |  |  | 0
35 | 13-06 | Applying lacquer polish to wood work of any type | M2 | 45.03 |  |  | 0
36 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 38.4 |  |  | 0
Metal Work
37 | 12-66 | Supply and Fixing of double glazed aluminium (color as approved) Premium model (Gauge 2 mm) 4" sect. Sliding window, including all necessary fittngs and fly screen shutters complete. | M2 | 28.67 |  |  | 0
38 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | M2 | 28.67 |  |  | 0
39 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | M | 2.1 |  |  | 0
40 | 25-44 | Supplying and Fixing 18SWG Steel Almirah, 12" max depth including box shelves, back, shelves, lock, spray paint complete | M2 | 18.31 |  |  | 0
Roofing & Water Proofing
41 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 208.32 |  |  | 0
42 | 09-16 | Khuras on roof 2'x2'x6" | Each | 3 |  |  | 0
43 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 3 |  |  | 0
44 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 56.58 |  |  | 0
45 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 56.58 |  |  | 0
46 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 56.58 |  |  | 0
47 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 56.58 |  |  | 0
NON SCHEDULE ITEMS-B
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 6.4 |  |  | 0
Entrance Steps / Podium
2 | N.S | Providing and fixing 3/4" thick pre-polished Granite Marble Slab uniform texture full width area above 2 sft laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges complete in all respect as approved / directed by The Engineer. | M2 | 3.22 |  |  | 0
Stair Steps
3 | N.S | Providing and laying Pre-polished Black Granite one-piece marble slabs Kitchen / Vanity Counter etc; laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment, making rounding edge and chemical polishing etc; complete in all respect, as per drawings and Specifications, sample as approved by The Engineer. | M2 | 1.52 |  |  | 0
Miscellenious
4 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 19.2 |  |  | 0
5 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 3 |  |  | 0
6 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 3 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 18-Mechanical (workshop)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 18: WORKSHOP
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Single-Girder Bridge Cranes
Providing, installing, testing and commissioning Top-Running Single-Girder Bridge Cranes, of internationally reputed approved make, complete with all its moving components, drives, drive controls, safety mechanisms, cables, cables collapsing mechanisms, operation-control equipment, and side rails, to be supported on the structure, including all jointing, fixing & installation accessories, initial charging of lubricants, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | In WORKSHOP: Capacity: 2 Tons | Nos: | 1
|  | Providing Tools and equipment as per requirment to development of the workshop or directed by the Engineer | LS | 1
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 18-electrical (Workshop)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 18: WORKSHOP
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.78 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 128.05 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 42.68 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.15 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.72 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 18.29 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 6 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 36.59 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 36.59 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 6 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-k-01 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 2x2000 lumens, complete in all respects | Nos. | 12 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 6 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 4 |  |  | 0
A.14 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
| 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" Wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 21.34 |  |  | 0
A.15 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 1 |  |  | 0
A.16 |  | Fire Extinguisher
| 14-145-a | Providing and fixing of Dry powder type Fire Extinguisher of approved quality and manufacturer best design including all fittings complete in all respects: 6kg | Each | 2 |  |  | 0
| 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 2 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 19-Summary (OR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 19: OPERATOR ROOM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
3 | PLUMBING WORKS | 0
TOTAL AMOUNT RS |  | 0

## 19-Civil (OR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 19: OPERATOR ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation in Common Material by mechanical means | M3 | 48.56 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 32.37 |  |  | 0
Anti-Termite
3 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | M2 | 265.58 |  |  | 0
Plain and Reinforement Concrete
4 | 06-03-b | Cement Concrete (brick/stone ballast, 1.5" to 2"/nullah shingle well graded and cleaned) in foundation & plinth (Ratio 1:4:8) | M3 | 7.9 |  |  | 0
GROUND FLOOR
5 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 11.38 |  |  | 0
Steel Reinforcement
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 0.96 |  |  | 0
7 | 06-26-a-02 | Damp proof course of cem. conc. 1:2:4 including bitumen coat, 1 layer polythene & 1 coat bitumen (2" thick) | M2 | 10.75 |  |  | 0
8 | 06-30-a-04 | V. Damp proof c/s plaster, 1 layer polythene 1 coat bitumen Ratio 1:3 (0.75" thick) | M2 | 10.75 |  |  | 0
Brick Work
9 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 23.26 |  |  | 0
GROUND FLOOR
10 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | M3 | 39.31 |  |  | 0
Flooring
11 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 54.94 |  |  | 0
12 | 10-03-b | Provide, lay, water & ram brick ballast 1.5" to 2" guage mixed with 25% sand for floor foundations | M3 | 7.07 |  |  | 0
13 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 2.39 |  |  | 0
14 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 47.17 |  |  | 0
15 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 5.53 |  |  | 0
16 | 10-51 | Providing and Fixing of Ceramic Tiles 12"×24" of Imported Approved Quality with jointing and finishing | M2 | 6.9 |  |  | 0
17 | 10-42 | Providing and fixing on walls1/4"(6mm approx.) thick of imported first grade ceramic tiles of size 24 in x 24 in of approved colour on walls, over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | M2 | 15.75 |  |  | 0
Surface Rendring
18 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) (ceiling plaster ) | M2 | 34.02 |  |  | 0
19 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 171.62 |  |  | 0
20 | 11-09-c | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | M2 | 117.61 |  |  | 0
Wood Work
21 | 12-56-b | Providing and fixing 1.5" (38 mm) thick pressed veneered door shutters fully flushed with First class wood veneering on all faces and sides fixed over partal wood cavited core and frame work of not less than 4" (100mm) wide strips all round with approved iron hinges, tower bolts as required. | M2 | 8.18 |  |  | 0
22 | 12-70-a | Supply and Fixing MS Sheet 16 guage(10'' x 2'') box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc | M | 20.7 |  |  | 0
23 | 12-24-a-01 | Extra for providing/fixing approved quality Rim locks : Imported | Each | 4 |  |  | 0
24 | 12-22-a-01 | Providing and fixing sliding bolt to doors Iron sliding bolts : 10" long | Each | 3 |  |  | 0
25 | 12-78-a | Kitchen Floor Cabinet as per MES Design/Specification. | M2 | 1.52 |  |  | 0
26 | 12-78-b | Kitchen Wall Cabinet as per MES Design/Specification. | M2 | 1.1 |  |  | 0
Painting and Warnishing
27 | 11-20-a | Priming coat of chalk under distemper | M2 | 215.92 |  |  | 0
28 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 215.92 |  |  | 0
29 | Ch-13 item 25-a+(bx2) P-102 | Preparing surface & painting with snowcem / weathershield paint: 3 Coats | M2 | 123.49 |  |  | 0
30 | Ch-13 item 03-c-01+(c-02x2) P-100 | Prepare & Paint new surface, doors & windows: 3 Coats | M2 | 16.35 |  |  | 0
Metal Work
31 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 7.68 |  |  | 0
Roofing & Water Proofing
32 | Ch-9 item 06+13 P-56&57 + Ch-6 item 28 P-34 | Single layer of tiles 10"x5"x1.25" laid over 4" earth and 1" mud plaster on top of RC roof slab, provided with 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft.i/c P/L Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) | M2 | 73.9 |  |  | 0
33 | 09-16 | Khuras on roof 2'x2'x6" | Each | 1 |  |  | 0
34 | 09-17 | Bottom khuras of brick masonry in c/s mortar 1:6,4'x2'x4.5" over 3" cem. concrete 1:4:8 | Each | 1 |  |  | 0
35 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 25.16 |  |  | 0
36 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 25.16 |  |  | 0
37 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 25.16 |  |  | 0
38 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 25.16 |  |  | 0
NON SCHEDULE ITEMS
Windows Sill
1 | N.S | ProvidinProviding and fixing 1/2" thick Pre-polished Sunny White Marble Slab uniform texture full width area above 3-8 sft laid ove 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment i/c beveling charges on exposed edges, complete in all respect as approved / directed by The Engineer. | M2 | 2.08 |  |  | 0
2 | N.S | Providing and laying Pre-polished Black Granite one-piece marble slabs Kitchen / Vanity Counter etc; laid over 3/4" thick cement sand mortar (1:2) i/c filling joints in white cement & matching pigment, making rounding edge and chemical polishing etc; complete in all respect, as per drawings and Specifications, sample as approved by The Engineer. | M2 | 1.1 |  |  | 0
Miscellenious
3 | N.S | Supply, provide and fix in position uPVC rain water down pipe lines conforming to ISO 3633:1991 and BS 3505 1968 (wall thickness 3.2mm) including proper joints complete in all respects, and system leak-free:
|  | 4" dia | M | 9.6 |  |  | 0
4 | N.S | Provide and fix uPVC plain bends with grating (as rain water inlets at roof), water tight connection leak-free:
|  | 4" dia | Each | 1 |  |  | 0
5 | N.S | Provide and fix uPVC shoe bends (as rain water outlets), water tight connection leak-free
|  | 4" dia | Each | 1 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 19-Electrical (OR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 19: OPERATOR ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 73.17 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 18.29 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 128.05 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 42.68 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 134.15 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 44.72 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 1 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 27.44 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 9.15 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 41.16 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 13.72 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 54.88 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 18.29 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.17 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 24.39 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 24.39 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 7 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 128.05 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 42.68 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 42.68 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 7 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 36.59 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 12.2 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 12.2 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 2 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | No | 6 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 12 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 4 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | No | 2 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | No | 2 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 2 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | Nos. | 1 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | M | 9.15 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, Distribution Boards, complete with all metering with indication lamps complete in all respects as per SLD. | Each | 1 |  |  | 0
A.17 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 1 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 19-Plumbing(OR)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 19: OPERATOR ROOM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
PLUMBING WORKS
Indian W.C
1 | 14-03-a | Providing and fitting glazed earthenware water closet (WC), squatter type (orisa pattern) combined with foot rest. complete in all respects : White | Each | 1 |  |  | 0
2 | 14-10-a | Providing and Fixing glazed earthen ware low down flushing cistern 3 gallons (13.63 Liters) capacity including bracket set, copper connection,etc. complete in all respects: White | Each | 1 |  |  | 0
3 | 14-05-a-01 | Providing and Fixing glazed earthen ware wash hand basin (WHB) complete size 56x40 cm (22"x16"), including bracket set, waste coupling, complete in all respects: White with pedestal (Best Quality) | Each | 1 |  |  | 0
4 | 14-102 | Providing & Fixing of SHOWER SET locally made complete with concealed T-STOP COCK for cold and hot water supply with mixer, swivel shower rose, long bib cock etc Complete in all respect. | Each | 1 |  |  | 0
5 | 14-27-a | Providing and fixing chorimum plated (CP) mixing valve for wash hand basin (WHB), sink or shower of approved (Best) quality | Each | 3 |  |  | 0
6 | 14-06-a | Providing and Fixing stainless steel sink with drain board size (120 x 60 cm) 48"x24", including set of brackets, waste pipe etc - (Best Quality) | Each | 1 |  |  | 0
7 | 14-13 | Providing and fixing choricum plated soap dish complete. | Each | 2 |  |  | 0
8 | 14-16-a | Providing and Fixing chromium plated (CP) towel 60 cm (24") long and 2 cm (3/4") dia | Each | 2 |  |  | 0
9 | 14-17-a | Providing and fixing best quality looking glass 5 mm thick neatly fitted on masonry wall etc. as per instruction of Engineer In-charge complete. Mirror 60 x 45 cm (24"x18") size | Each | 1 |  |  | 0
10 | 14-21-c | Providing and fixing chromium plated (CP) double bib cock, heavy duty of approved quality : 1.5 cm (1/2") | Each | 1 |  |  | 0
11 | 14-25-a | Providing and fixing chromium plated (CP) tee stop cock 1.5 cm (1/2") of approved quality | Each | 3 |  |  | 0
12 | 14-31-a | Providing and Fixing cast iron (CI) floor trap of approved quality including CI grating & concrete chamber all round : 4"x2" (100mm x 50 mm) | Each | 3 |  |  | 0
13 | 14-33 | Providing and Fixing 4" gully trap of approved quality including cement concrete cost of PVC grating 6" x6" (150 x 150 mm) and masonry chamber 12"x12" (300 x 300 mm). | Each | 1 |  |  | 0
14 | 14-157 | P-Trap (uPVC) for squatting type WC.
| 14-157 | ii) 10 cm (4") glazed. | Each | 1 |  |  | 0
SEWERAGE SYSTEM
15 | 14-95-a | Making connection with the existing system PVC pipe line including cutting the pipe for providing & fixing required fittings : Class B PVC
|  | a) 3" i/d (75 mm) | m | 20 |  |  | 0
|  | b) 4" i/d (100 mm) | m | 20 |  |  | 0
|  | d) 6" i/d (150 mm) | m | 20 |  |  | 0
Non SCHEDULE ITEM
1 | NS-1 | Providing, fixing, jointing and testing Polypropylene Random (PPR) PN20 pressure pipe for cold, hot and hot water return water as per DIN 8077-8078 for pipes and DIN 16962,PN25 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, walls cutting for pipelines, complete in all respect as per specifications and drawings as well as directed by the Engineer.
|  | 20 mm dia | m | 25 |  |  | 0
|  | 25 mm dia | m | 20 |  |  | 0
|  | 32 mm dia | m | 20 |  |  | 0
2 | NS-2 | Providing and making Manhole 2'x2' internal size including 9" thick brick masonry (1:4), 1/2" th. Plastering (1:3) i/side, benching with PCC 1:2:4 4" th. with cement finish, excluding manhole cover, complete in all respects. | Each | 2 |  |  | 0
3 | NS-3 | Providing and fixing food grade plastic over head water tank (200 gallon) including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Each | 1 |  |  | 0
SUB TOTAL OF PLUMBING WORKS | [6 empty] | 0

## 20-Summery(Main Gate & Boundry)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 20: MAIN GATE & BOUNDRY WALL
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 20-Civil(Main Gate & boundry)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 20: MAIN GATE & BOUNDRY WALL
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-a | Structural Excavation in Common Material by mechanical means | M3 | 2475 |  |  | 0
2 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 1732.5 |  |  | 0
3 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 165 |  |  | 0
4 | 06-07-a-02 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1.5:3) | M3 | 928.12 |  |  | 0
5 | 06-07-b-02 | RCC in raft foundation slab, base slab of column & ret.wall etc, not including in 06- 06 (1:1.5:3) | M3 | 1035.18 |  |  | 0
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 2771.4 |  |  | 0
7 | 25-30-b | Providing and fixing steel grated doors, complete with locking arrangement, angle iron frame 2"x2"x3/8" and 1" square bars 4" center to center. | M2 | 72 |  |  | 0
8 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 1732.5 |  |  | 0
9 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 1732.5 |  |  | 0
10 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 1732.5 |  |  | 0
11 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 1732.5 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 21-Summary (Ext. PL)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 21: EXTERNAL PIPING
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 21-Civil(PPL)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 21: EXTERNAL PIPING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-49-b | Excavation in open cut for sewers & manholes except shingle, gravel & rock : 2m to 5m | M3 | 2100 |  |  | 0
2 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 10500 |  |  | 0
3 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 10500 |  |  | 0
4 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 10500 |  |  | 0
5 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 10500 |  |  | 0
6 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 10500 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 21-Mechanical (PPL)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 21: EXTERNAL PIPING
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | DN-180 HDPE PIPE
Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 (180mm) ( including fittings and Bends etc)
|  | HDPE Pipe | M | 432 |  |  | 0
2 | NS-2 | DN-1200 HDPE PIPE
Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 1200mm ( including fittings and Bends etc)
|  | HDPE Pipe | M | 306 |  |  | 0
3 | NS-3 | DN-900 HDPE PIPE
Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 900mm ( including fittings and Bends etc)
|  | HDPE Pipe | M | 462 |  |  | 0
4 | NS-4 | DN-1000 HDPE PIPE
Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-10 1000mm ( including fittings and Bends etc)
|  | HDPE Pipe | M | 336 |  |  | 0
5 | NS-5 | Sluice Valves
Sluice Valves with all acessories complete in all respect for various pipe sizes as shown on the drawings
HDPE Pipe Line
|  | 800mm | No | 7 |  |  | 0
|  | 900mm | No | 12 |  |  | 0
|  | 1000mm | No | 6 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0

## 22-Summary (Ext El)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 22: EXTERNAL ELECTRIFICATION
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 22-Civil (Ext. Elec)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 22: EXTERNAL ELECTRIFICATION
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-25-b | Excavation in foundation of building, bridges etc complete : in ordinary soil | M3 | 289 |  |  | 0
2 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | M3 | 212 |  |  | 0
Plain and Reinforement Concrete
3 | 06-03-b | Cement Concrete (brick/stone ballast, 1.5" to 2"/nullah shingle well graded and cleaned) in foundation & plinth (Ratio 1:4:8) | M3 | 42 |  |  | 0
4 | 06-07-b-03 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:2:4) | M3 | 58 |  |  | 0
5 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) | M3 | 26 |  |  | 0
Steel Reinforcement
6 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 7.4 |  |  | 0
Brick Work
7 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | M3 | 54.1 |  |  | 0
Surface Rendring
8 | 11-09-b | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 375.8 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 22-Electrical (Ext. E)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 22: EXTERNAL ELECTRIFICATION
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
2 |  | LT CABLES
Supply at site, installation, testing & Commissioning of following under mentioned PVC insulated unarmoured copper conductor cable 600 /1000 Volt grade manufactured by any one of the manufacturers as mentioned in appendix in prelaid conduits/ trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects. manufacturers as specified in Annexure “A” Actual length of cables to be installed shall be measured at site by the Contractor, duly authenticated by the employers electrical engineer before placing the order with the manufacturer, however, approximate length of cables are shown herewith. Payments shall be made as per actual length installed
| 15-123-a | b) 3-Core 2.5mm2 PVC/PVC Copper Conductor Cable between pole base Connection box to light fixtur | M | 1800 |  |  | 0
ii |  | Circuit Protective Conductor (CPC)
| 15-48-d | 1 CORE 16mm sq | M | 2020 |  |  | 0
| 15-48-c | 1 CORE 6mm sq | M | 1295 |  |  | 0
| 15-48-b | 1 CORE 2.5mm sq | M | 1350 |  |  | 0
3 |  | ROUND CONICAL POLE
3.1 | 26-01-a-04 | Single arm round conical Pole, hot dipped galvanized (80 microns) 8 meters overall thickness 4mm Arm length 1.5 meters each with OD 60 mm, base dia 180 mm and top dia 75mm with base plate arrangement (400mm x 400 mm x 20mm), 4 No of Stiffners (200mm x 100mm x 20mm), complete in all respects | Each | 72 |  |  | 0
3.2 | 26-01-a-03 | Double arm round Conical Pole, hot dipped galvanized (80 microns) 8 meters overall thickness 4mm Arm length 1.5 meters each with OD 60 mm, base dia 180 mm and top dia 75mm with base plate arrangement 400mm x 400 mm x 20mm, 4 No of Stiffners (200mm x 100mm x 20mm), complete in all respects | Each | 4 |  |  | 0
3.3 | 15-35-g | Providing and laying of cable route marker cast iron for all sort of Road Light, Street Lights & Boundary Wall lights complete in all respects with all installation material complete | Each | 54 |  |  | 0
4 |  | STREET LIGHT FIXTURES
4.1 | 15-36-e | Supply & erection of SMD Type LED Road light Fixture (90-100 watts) | Each | 80 |  |  | 0
4.2 | 15-36-l-01 | Supply & Erection of candle flood light 150 watt complete in all aspects | Each | 12 |  |  | 0
5 |  | MAN HOLE
| 15-42-b | Manhole For LT Cable Pulling | Each | 30 |  |  | 0
6 |  | CABLE TRAY
| 15-135-b | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long, 12" wide with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects. | M | 60.9756 |  |  | 0
NON SCHEDULE ITEMS
1 |  | 11 KV WAPDA GRID PANEL
Supply, installation and energizing of HT Grid Panel factory fabricated & tested, manufactured by (SIMENS / AREVA / PEL / FICO make only) consists of 12 SWG mild steel sheet fabricated floor mounted free standing 1-cubical, indoor type (IP-54) totally enclosed with hinged front doors. The panel designed suitable for 11 KV 3-phase, (3-wire) 50 Hz AC system, high conductivity, hard drawn electrolytic copper bus bars of adequate current carrying capacity and short circuit rating copper interconnections, internal wiring and cable termination arrangements using HT Raychem Heat Shrinkable Termination Kit (German) for 3 core HT Armoured cable of appropriate size as per WAPDA specifications (P-44:96) and finished with RAL-7032 powder coating baked. Equiped with following components (All components used should be from WAPDA approved list)
Components 1 No. 11KV VCB 630A 17.5KV 25KA with drawout type (Make Hyundai / Eqv) 1 No. Electronics IDMT/S/C, O/C, E/F Relay/TEST Block (Make Areva/GE) 3 Nos. 11KV Current Transformers (Make FICO) 400:200/5AFor Protection 3 Nos. 11KV Current Transformers (Make FICO) 400:200/5AFor Metering 3 Nos. Voltage Transformer 11KV/110V (Make FICO) 1 No. Ampere Meter 0-100/400A (Make Lumel / Frer) 1 No. Ampere Selector Switch 4-position (Make GGT/Merz) 1 No. Volt Meter 96x96 0-15KV (Make Lumel / Frer) 1 No. Volt Selector Switch 4-position (Make GGT/Merz) 2 Nos. Push Button 25MM For VCB (Make Telemecanique) 4 Nos. Indication Lamp 25MM 110VAC/110VDC (Make Telemecanique) 1 No. 6A Control MCB TP 6KA (Make ABB/GE) 4 Nos. 6A Control MCB DP 6KA (Make ABB/GE) 1 No. Auxiliary Contact 2NO+2NC (Make ABB/GE) 1 No. Auxiliary Contact 2NO+2NC (Make ABB/GE) 1 No. DC supervision Relay (Make E-Lab) 3 Nos. Surge Arrester 5 To 15kv (Make Chint) 15 Set 11kv Insulator for Fitting Arrangement Bus Bar (Make Jeorjordan) 1 Set Control & CTs Terminal Block (Make Kelmsion/Wiland) 126 Cft 10/12SWG Powder Painted 01-Cubicles. Size 7'.2"x3'x6' each 230 Kg 2500A Electrolytic Copper bus bar for main & link. Size as per WAPDA standred 3x2x100x10MM Main Bus Bar as Per P-44:96 8 Nos. 1-1/2" Fibre glass insulator for bus bar mounting
| Appendix-C Electrical Works Page 1 | 1 L/S Wiring, wiring cables, thibmles, sleaves, cable tray and other wiring accessories. Complete in all respect as per satisfaction of the Engineer Incharge. | Each | 1 |  |  | 0
2 |  | 11 KV WAPDA METERING PANEL
Supply , installation , and energizing of HT Metering Panel factory fabricated & tested, manufacture by SIEMENS, PEL, PEMPAK ,FICO MAKE only, consist of 12 SWG mild steel sheet fabricated floor mounted free standing one cubical indoor type (I.P 54) total enclosed with hinged front doors, the panel designe suitable for 11KV three phase 50 Hrz AC system, high conductivity, hard drawn electrolytic copper bus bars of adequate curren carring capacity and short circuit raiting copper interconnections, internal wiring and cables, termination arrangements, using HT Raycherm Heat Shrinkable termination kit German for 3 core HT Armoured cable of appropriate size as per wapda spacification and fineshed with RAL- 7032 powder coating baked. Equiped with following compnents (All components used should be from WAPDA approved list).
1 No. 11KV VCB 630 Amps 17.5 KV 25 KA with drawout type. (Make Hyndai or Equ.) 1 No. Electronics IDMT/S/C, O/C, E/F Relay / TEST Block. (Make Areva or Micro or Equ.) 3 Nos. 11 KV current transformers.(Make FICO or Equ.) 400:200 /5A for protection. 3 Nos. 11 KV current transformers. (Make FICO or Equ.) 400:200 /5A for metering. 3 Nos. Voltage transformer 11kv/110 V.(Make FICO or Equ.) 1 No. Ampere meter 0-100/400A. (Make Lumel or Frer) 1 No. Ampere selector switch 4-position.(Make Merz or Bretler) 1 No. Voltmeter 96x96 0-15 KV. (Make Lumel or Frer) 1 No. Volt selector switch 4-position.(Make Merz or Bretler) 2 Nos. Push button 25mm for VCB. (Make Telemecanique) 4 Nos. Indication Lamp 25mm 110 VAC/110 VDC. (Make Telemecanique) 1 No. 6A control MCB TP 6KA (Make ABB or GE) 2 Nos. 6A control MCB DP 6KA. (Make ABB or GE) 1 No. Auxiliary Contact 2NO+2NC (Make ABB or GE) 1 No. Auxiliary Contact 2NO+2NC (Make ABB or GE) 1 No. Capacitor Trip Unit. (Make E-Lab) 9 Set 11KV insulator for fitting arangement Bus Bar (Make Jeorjordan) 1 Set Control and CTs terminal Block. (Make Kelmsion/ Wiland) 126 Cft 10/12 SWG Powder Painted 01- Cubical Size 7'.2"x3'x6' Each 90 Kg 2500A Electrolytic copper bus bar for main & link size as per wapda stander 3x2x100x10mm main bus bar as per P-44:96 4 Nos. 1-1/2" fiber glass insulator for bus bar mounting. 1 L/S Wiring, wiring cables, Thimbels, Sleaves, Cable Tray or other wiring Accessories.
| Appendix-C Electrical Works Page 2 | complete in all respect, as per satisfaction of the Engineer Incharge. | Each | 1 |  |  | 0
3 | Appendix-C Electrical Works Page 3 | HT. CONSUMER/PROTECTION PANEL
Supply , installation , testing and commissioning of HT consumer / protection panel factory fabricated and tested, manufacture by SIEMENS, PEL, PEMPAK ,FICO MAKE only, consist of 12 SWG mild steel sheet fabricated floor mounted free standing one cubical indoor type (I.P 54) total enclosed with hinged front doors, the panel designe suitable for 11KV three phase 50 Hrz AC system, high conductivity, hard drawn electrolytic copper bus bars of adequate curren carring capacity and short circuit raiting copper interconnections, internal wiring and cables, termination arrangements, using HT Raycherm Heat Shrinkable termination kit German for 3 core HT Armoured cable of appropriate size as per wapda spacification and fineshed with RAL- 7032 powder coating baked. Equiped with following compnents (All components used should be from WAPDA approved list).
|  | 1 No. 11KV VCB 630 Amps 17.5 KV 25 KA complete.(Make Hyundai/Equ) 1 No. Electronics IDMT/S/C, O/C, E/F Relay.(Make Areva/GE) 3 Nos. 11 KV current transformers.(Make FICO) as per suatiable raiting for protection. 3 Nos. Voltage transformer 11kv/110 V. (Make FICO) 1 No. Ampere meter 0-100/400A.(Make Lumel) 1 No. Ampere selector switch 4-position.(Make GGT/Merz) 1 No. Voltmeter 96x96 0-15 KV (Make Lumel) 1 No. Volt selector switch 4-position.(Make GGT/Merz) 2 Nos. Push button 25mm for VCB.(Make Telemecanique) 4 Nos. Indication Lamp 25mm 110 VAC/110 VDC.(Make Telemecanique) 1 No. 6A control MCB TP 6KA (Make GE/ABB) 2 Nos. 6A control MCB DP 6KA (Make GE/ABB) 1 No. Auxiliary Contact 2NO+2NC (Make GE/ABB) 1 No. Auxiliary Contact 2NO+2NC (Make GE/ABB) 1 No. Capacitor Trip Unit. (Make Chint) 9 Sets 11KV insulator full fitting arangement Bus Bar.(Make Jeorjordan) 1 Set Control and CTs terminal Block. (Make Kelmsion) 126 Cft 10/12 SWG Powder Painted 01- Cubical Size 7'.2"x3'x6' Each 90 Kg 630A Electrolytic copper bus bar for main & link size as per wapda stander 40 Nos. 1-1/2" fiber glass insulator for bus bar mounting. 1 L/S Wiring, wiring cables, Thimbels, Sleaves, Cable Tray or other wiring Accessories. complete in all respect, as per satisfaction of the Engineer Incharge. | Each | 1 |  |  | 0
4 |  | Transformer (Oil Type)
Supply at site, installation, testing and commissioning of new step down Distribution transformer pad mounted oil type manufactured according to BSS-171, IEC-76 or VDE-0532/NTDC-WAPDA relevent standards and, specifications and consisting of the under mentioned items.
Filling device, drain plug, oil level indicator, lifting hooks, bi-directional roller wheels, H.V. & L.V. porcelain bushings, off load tap changer, 2 earthing terminals, conservator and silica gel breather, thermometer pocket with digital thermometer, imported double float buckholz relay to be connected with VCB Input of Consumer panel, pressure relief vent, digital thermometer with alarm & trip contacts, rated Voltage 11000 / 415 / 230 Volts, suitable for an ambient temperature of 50°C , impedance 6% or as specified by IEC, system earth: Delta-Y, neutral solidly earthed (DYN- II), transformer oil, I.P - 54. The transformer shall be suitable for loading of 100% continuous maximum rating with “ONAN” cooling without exceeding the thermal limit. all necessary accessories / materials, including submission of technical data sheet, complete in all respects and as approved by the Engineer.
| Appendix-C Electrical Works Page 4 | 3000 KVA Transformer Including cost of Foundation | Each | 1 |  |  | 0
5 |  | Horizontal Thrust Boring
| Appendix-C Electrical Works Page 5 | Provision of horizontal thrust boring at road crossing including UPVC 6" dia pipe (C-Class), back filling and compaction for H.T / L.T cables and crossing where road crossing sleeves are not available as per site requirement and approval of the Consultant . * subject to actual site work | M | 33 |  |  | 0
6 |  | H.T cables
Supply at work, laying, testing and commissioning of following H.T cables, laying directly in the sand layer, in already excavated trenches or through duct and/ or PVC pipe (already provided), including cable binding ties as per specifications, standards, and drawings and to the of the Consultant . Make Pakistan Cables, Newage Cables or eqv.
| Appendix-C Electrical Works Page 6 | 185 MM2 AL/XLPE/AWA/PVC 15 KV 3X single core aluminium cable | M | 600 |  |  | 0
7 |  | HT terminations kits
Supply at work, installation testing & commissioning of following HT terminations kits, Raychem /3-M/Cellpack for cables laid under works in above Item , including cable glands and miscellaneous material and installations as per requirements specifications and standards and to the approval of the Consultant .
| Appendix-C Electrical Works Page 7 | 70 MM2 AL/XLPE/AWA/PVC 15 KV single core aluminium cable | Each | 18 |  |  | 0
8 |  | Cable Markers
| Appendix-C Electrical Works Page 8 | Supply at works & installation of HT & LT cable markers (concrete) as per specifications, drawing and approval of the Consultant . | Each | 70 |  |  | 0
9 |  | 3000 KVA GEN. SET
Supply at site, installation, testing and commissioning at designated location, connection of cables, testing and commissioning of water cooled NEW diesel generating sets suitable for operation at 50oC and 90% relative humidity manufactured by any one of the manufacturers as specified in annexure “A” assembled in accordance with their provided drawings / manuals and consisting of painted welded steel bed plate frame work to accommodate engine alternator complete with electronic governor to give regulation to BS: 514 class A1, balanced flywheel, water jacket heaters energized by the in coming main supply, heavy duty starting batteries, battery charger,
set of spare oil/fuel filters engine panel with oil pressure and water temperature gauge, pressure and water temperature gauge, (Electrical), alternator electronic voltage regulator, radio interference suppressors, electronic tachometer frequency meter voltmeter with selector switch, Ammeter with selector switch, hour runs meter, KWH meter, KW (total and per phase) KVA total and per phase.
Power factor (Ave, total and per phase. KVAR (total) KVAR hour % of rated load, emergency stop push button, radiator, with water level switch, suitable for 400 / 230 volts, 50 cycles/second, at 1500 rpm, for 3 phase 4 wire system, including cost of all necessary material / accessories, daily fuel tank and conforming to technical specifications mentioned below.
| Appendix-C Electrical Works Page 9 | 3000 KVA Gen Set, Included cost of ATS Panel ,Sound Attenuated Canopy and Foundations. | Each | 1 |  |  | 0
10 |  | Earthing System
| Appendix-C Electrical Works Page 10 | Providing and installation of Earthing Veractor Cone / Spike Size 2" thick, 12" long as shown in drawings or ¾” dia & 10 ft long copper rod as earth electrode 100 ft or upto the water level, below ground level including cost of boring and lowering the rod (100ft / upto the water level) down, complete with clamp, test point copper plate 18" x 2.5" x 0.5" and 2x70mm2 stranded copper conductor from rod to ground surface in 2” dia G.I.pipe (EL Class) with watering cap, Man-hole with cover as per detail shown in drawings. all earth work should be done according to the advise of electrical consultant. | Each | 20 |  |  | 0
11 |  | AMR METER
| Appendix-C Electrical Works Page 11 | Supply, installtion testing and commissioning of AMR Meter as per WAPDA Specification complete in all respect and to the approval of the Consultant . | Each | 1 |  |  | 0
12 |  | AMR METER
| Appendix-C Electrical Works Page 12 | Supply, installtion testing and commissioning of Energy Meter as per WAPDA Specification complete in all respect and to the approval of the Consultant . | Each | 2 |  |  | 0
13 |  | Main Panel Board / MCC PANEL:
Supply of MPB made of sheet steel 12 SWG, totally enclosed, indoor free Standing design including all auxiliaries, internal wiring from Mccbs terminating on cable terminals blocks, Including provision of Cable Glands + Cable Lugs according to Sizes of Cables , designation labels of all incoming and outgoing feeders as shown on the drawings, earthing bar, neutral bar, suitable for system voltage 415 V, 50 Hz, 3 phase, neutral and earthing busbars made of 99.8% electrolytic copper of under mentioned capacities. Body of MPB shall be degreased and de-rusted having one coat of antirust paint with further 2 coats of powder paint of approved colour and shall be equipped as mentioned below, including cost of all necessary materials complete in all respects and accordance with the latest BS codes and conforming to single line diagram. Rated current of Main & Neutral Bus Bar rated at 50 degree centigrade All Breakers to be installed shall be of one make only and not mixture of two manufacturers. Make MG. (Made in France), Mitsubishi and Terasaki (Made in Japan/Spain) ABB, Legrand, GE/AEG (Made in Italy ). Rated Ics not less than 35 KA for incoming , outgoing Breakers and for busbar installed in the Panel. Front & Rear open able doors. Shop drawings shall be submitted by the manufacturer for Approval to consultant before starting Fabrication of all Main Panel Board , Sub Main Panel Board Motor Control Centre and Light, Power Distribution Boards.
Including cost of Brass cable glades for incomming and outgoing cables.
13.1 | Appendix-C Electrical Works Page 13 | Main Panel Board / MCC PANEL: : Conforming to same constructional specifications as per item No. 2 mentioned above but equipped with the following: As shown in SLD. | Each | 1 |  |  | 0
13.2 |  | SYNCHRONIZING PANEL / ATS PANEL
| Appendix-C Electrical Works Page 14 | Conforming to same constructional specifications as per item No. 2 mentioned above but equipped with the following: As shown in SLD. | Each | 1 |  |  | 0
13.3 |  | P.F.I. PLANT
Supply, installation & commissioning of sheet metal clad totally enclosed free standing, front excess Power factor improvement plant to be installed with Main LT Switch Board, fabricated from 12 SWG M.S. sheet steel & doors from 14 SWG M.S. sheet steel with electrostatic paint of approved color, 415 volts, 3 phase, 50Hz, power factor improvement plant of automatically / manually controlled. complete with air contactors, HRC fuses for short circuit protection.
On/Off push buttons, On/Off indication light, PFI relay, make Nokian for switching in & out out the capacitors in , control fuses, auto/manual selector switch, 415 volts 3 phase delta connected capacitors make Gruppo Energia/Nokian and ON/OFF indicating lamps.
| Appendix-C Electrical Works Page 15 | 800 KVAR, Complete in all respect as per single line diagram. | Each | 1 |  |  | 0
13.4 | Appendix-C Electrical Works Page 16 | DB1-GF & DB2-GF: Conforming to same constructional specifications as per item No. 2 mentioned above but equipped with the following: As shown in SLD. | Each | 2 |  |  | 0
13.5 | Appendix-C Electrical Works Page 17 | DB-GEN. ROOM, DB-CHORINE BULDING,DB-SAND FILTER,DB-OPERATOR QUARTER,DB-ADMIN BULDING,DB-ELECT. ROOM, DB-WORKSHOP, DB-GUARD: Conforming to same constructional specifications as per item No. 2 mentioned above but equipped with the following: As shown in SLD. | Each | 7 |  |  | 0
13.7 | Appendix-C Electrical Works Page 39 | DB-VALVES & GATES: Conforming to same constructional specifications as per item No. 2 mentioned above but equipped with the following: As shown in SLD. | Each | 4 |  |  | 0
14 |  | STREET LIGHT CONTROL PANEL
| Appendix-C Electrical Works Page 18 | Supply ,installation testing & commissioning of Road Light Control Panel 16 SWG sheet steel construction with IP 43 protection class, canopy, door, locking arrangement with MCCB magnetic contactor relay. Photo cell, control swiches and monitoring switches etc including provision of brick masonry foundation with PCC 3" Thick top pad, as per drawing, and approval of the consultant/the Engineer Detail is as under. Manufactured by any one of the manufacturers Siemens, PEL,TechnoBuild Engineering.
Incoming
1-100 A MCCB TP RC:16KA
outgoing
|  | 10-30A MCB TP RC:6KA | Each | 1 |  |  | 0
15 |  | POLE BASE CONNECTION BOXES
| Appendix-C Electrical Works Page 19 | Supply , Installation, testing and commissioning oF Pole Base Connection Boxes complete comprising 2-NO.circuit breakers (MCB 6A,)connectors, nut & bolts etc; as per drawings, specification, complete in all respects and to the approval of the Consultant/The Engineer: Make TechnoBuild Engineering, PEL, Siemens.
|  | a. Connection Box | Each | 18 |  |  | 0
16 |  | LT CABLES
Supply, Laying, testing and commissioning of LT Copper Conductor Cable, PVC insulated, PVC sheathed 660/1100 volt grade cable, armoured with G.I. wire 16 SWG. laid directly in the already excavated as per item B-1, including 2'' UPVC pipe at road crossing with provision of warning tape as per drawings, specifications and approval of the consultant/the Engieer, Make Pakistan Cables, Newage Cables, Fast Cables or eqv.
16.1 | Appendix-C Electrical Works Page 20 | 150 mm2 4-core cable, | M | 890 |  |  | 0
16.2 | Appendix-C Electrical Works Page 21 | 120 mm2 1-core cable, | M | 5920 |  |  | 0
16.3 | Appendix-C Electrical Works Page 22 | 120 mm2 4-core cable, | M | 260 |  |  | 0
16.3 | Appendix-C Electrical Works Page 23 | 50 mm2 4-core cable, | M | 390 |  |  | 0
16.4 | Appendix-C Electrical Works Page 24 | 35 mm2 4-core cable, | M | 760 |  |  | 0
16.5 | Appendix-C Electrical Works Page 25 | 25 mm2 4-core cable, | M | 1260 |  |  | 0
16.6 | Appendix-C Electrical Works Page 26 | 16 mm2 4-core cable, | M | 100 |  |  | 0
16.6 | Appendix-C Electrical Works Page 27 | 10 mm2 4-core cable, | M | 1295 |  |  | 0
16.7 | Appendix-C Electrical Works Page 28 | 6 mm2 4-core cable, | M | 4052 |  |  | 0
16.7 | Appendix-C Electrical Works Page 29 | 16 mm2 2-core cable, | M | 540 |  |  | 0
16.7 | Appendix-C Electrical Works Page 30 | 10 mm2 2-core cable, | M | 1576 |  |  | 0
16.7 | Appendix-C Electrical Works Page 31 | 6 mm2 2-core cable, | M | 1576 |  |  | 0
16.9 | Appendix-C Electrical Works Page 32 | 4 mm2 2-core cable, From LT Main Panel Board to CONVEYER, FINE SCREENS, PUMP ROOM, SUMP PUMP, & PENSTOCKS. | M | 36400 |  |  | 0
ii |  | Circuit Protective Conductor (CPC)
16.1 | Appendix-C Electrical Works Page 33 | 1 CORE 70mm sq | M | 14140 |  |  | 0
16.1 | Appendix-C Electrical Works Page 34 | 1 CORE 50mm sq | M | 390 |  |  | 0
16.1 | Appendix-C Electrical Works Page 35 | 1 CORE 25mm sq | M | 390 |  |  | 0
16.11 | Appendix-C Electrical Works Page 36 | 1 CORE 10mm sq | M | 2120 |  |  | 0
16.12 | Appendix-C Electrical Works Page 37 | 1 CORE 4mm sq | M | 4052 |  |  | 0
17 |  | BUS TIE DUCT
Supply at site, fabrication and installation of Following TP+N+E Bus Tie Duct Strict Compliance As Per IEC 61439-1, 2 & 6. Standard IP55 protection degree [EN60529], Pogliano brand Insulated Busbar Systems (ITALY), Complete in all respect, as approved by the Electrical Engineer.
| Appendix-C Electrical Works Page 38 | Copper Contact Aluminium Busway, 4000A, 3P+N+E, IP55 | M | 100 |  |  | 0
18 |  | PROVISION OF WAPDA CONNECTION
| As Per WAPDA rates 2020 | Design, approval from WAPDA, execution, testing and commissioning of 11 kV (single / composite arrangement on poles) overhead network for the Treatment Plant and associated works shall be included in the Contractor's scope of work. Contractor shall be responsible for complete site survey and design of HT feeder / network from the source 132/11 kV grid station(s) upto project premises / sites. The feeder extension from Grid Station for distribution transformers at the project premises/sites comprising of HT Allum ACSR Osprey conductors, 36 ft Steel Structure Poles, Cross arms, insulators, connecting hardware, terminations / jumpers, anti-climbing devices, danger sign, foundations, earthing etc. complete in all respect as per WAPDA prevailing rules and regulations. Including Cost of Security Deposit to WAPDA on the name of Client. | Job/ PS | 1 | 36046411.52 | - | 36046411.52
19 |  | ENHANCEMENT OF 132/11.5 KV GIS GRID STATION
|  | Design, approval, supply, installation, testing commissioning of Enhancement of 132/11.5 KV GIS Grid Station including cost of 132/11.5 KV, 20/26 MVA Power Transformer 50Hz, 10% Impadence, Vector Group Dyn11, On Load Tap Changer Aux:Panel (Extended Creepage Bushing) and required Termination Connectors, (Including Dehydration of Transformer Oil), 120 KV Metal Oxide (Gapless) Surge Arrestor with Surge Counter and Terminal connectors for 600 mm Sq Aluminum Conductor Including Steel supporting structure (Extended Creepage Porcelain Insulator), 145 KV -XLPE S/C, Copper Condutor,800 Sqmm Power Cable, 145KV -Cable Bushing with structure &Ternimal Connector, 132KV -Out Door Type Termination Kit for 145 KV -XLPE S/C, Copper Conductor, 800 Sqmm Power Cable, 132KV -GIS Termination(Plug-in-Type)for 145 KV -XLPE S/C, Copper Conductor, 800 Sqmm Power Cable, 12 KV Extended Creepage Surge Arrestors with surge counter and Terminal Connectors, complete 132 KV Steel Gantries & Hardware, complete 132 KV Control & Protection System, complete 132 KV Substation General Items, 15 KV XLPE Power Cables and terminations and control cables, Earthing Material Substation Grounding System for 132 kV Switch yard and Control house Building, 12 KV METAL CLAD (VCB-Type) Switchgear Panels, Battery Bank And Battery Charger and including all the items either explain in this description or not but necessary to complete this job, complete in all respect as approved by the Engineer Incharge and as per WAPDA/NTDC (updated) Specifications. NOTE: This is provisional item and if the load is available in the existing Grid Station this item will not be required. Otherwise contractor will bear Grid sharing charges including transmission charges complete in all respects for dedicated feeder for WTP Mingora | Job/ PS | 1 | 133975681 | - | 133975681
SUB TOTAL OF ELECTRICAL WORKS

## 23-Summary(RW)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 23: ROAD WORKS
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS (Internal Roads) | 0
2 | CIVIL WORKS (External Roads) | 0
TOTAL AMOUNT RS |  | 0

## 23-Civil (Int.RW)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 23: ROAD WORKS
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS (INTERNAL ROAD)
Earthwork for Maintain the Grading Plan
1 | 03-01-b | Earth excavation undressed upto single throw of kassi phaorah or shove etc : in ordinary soil, | M3 | 1938 |  |  | 0
2 | 03-29-b | Compaction of earth with power road roller 90% max. mod. AASHTO dry density | M3 | 865.45 |  |  | 0
3 | CH:3 item 03-20-a P-12 | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 1072.55 |  |  | 0
4 | CH:3 item 03-20-b P-12 | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 1072.55 |  |  | 0
5 | CH:3 item 03-20-c P-12 | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 1072.55 |  |  | 0
6 | CH:3 item 03-20-d P-12 | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 1072.55 |  |  | 0
Parking Shed
1 | 10-49-a | Providing and Fixing Precast Concrete 7000 psi TUFF Tiles 50mm thick over bed of 2" thick sand & 4" thick brick ballast/stone ballast complete. | M2 | 200 |  |  | 0
2 | 16-73-b | Providing and fixing kerb stone (12"x14"x6") in cement sand mortar 1:3 in center media or round about as specified. | M | 192 |  |  | 0
3 | 13-19 | Paint on Concrete work (Kerb stone, Barrier) | M2 | 69.12 |  |  | 0
4 | 25-58-c | Providing and fixing of parking shed consisting of fiber glass Sheet, tubular pipe frame (heavy) quality and circular columns excluding cost of foundation. | M2 | 200 |  |  | 0
5 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 0.67 |  |  | 0
Earthwork and Allied Activities
1 | 03-60 | Clearance of site by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, | M2 | 13651 |  |  | 0
2 | 03-65 | Compaction of Natural Ground | M2 | 13651 |  |  | 0
3 | 03-70-a | Formation of Embankment from Roadway Excavation in Rock Material requiring blasting and compaction Modified AASHTO 95% of embankment by power roller. | M3 | 3309.49 |  |  | 0
4 | 03-70-b | Formation of Embankment from Roadway Excavation in Rock Material requiring blasting and compaction Modified AASHTO 95% of embankment by power roller. | M3 | 3309.49 |  |  | 0
5 | 03-70-c | Formation of Embankment from Borrow Excavation in Common Material including compaction Modified AASHTO 90% by power roller. | M3 | 5482.76 |  |  | 0
Sub Base, Base Course & Surfacing
6 | 16-04-b | Granular Sub Base Using Crushed Stone Aggregate | M3 | 1598.12 |  |  | 0
7 | 16-05-b | Water Bound Macadam Base Course | M3 | 2130.83 |  |  | 0
8 | 16-06 | Providing and Laying road edging of 3" wide & 9" deep brick on end, complete | M | 2536.7 |  |  | 0
9 | 16-10-c | Triple bitumenous Surface Treatment | M2 | 319.62 |  |  | 0
Ancillary Works
S. No | MRS (2018) Reference | Description of Works | Unit | #VALUE!5 | Column1 | #N/A4 | #VALUE!44
10 | 10-49-a | Providing and Fixing Precast Concrete 7000 psi TUFF Tiles over bed of 2" thick sand & 4" thick brick ballast comp | M2 | 464.68 |  |  | 0
11 | 16-73-a | Providing and fixing kerb stone (12"x18"x6") in cement sand mortar 1:3 in center media or round about as specified. | M | 500 |  |  | 0
12 | 16-76-a | Pavement marking in reflective chlorinated rubber paint with glass beads for line 15 cm width. | M | 3042.6 |  |  | 0
13 | 16-25-a-02 | Supply and Fixing aluminium alloy road studs as per specs Large, strip 146x30mm, 171 beads: Uni-direction | Each | 328 |  |  | 0
14 | 16-20-a | Traffic Road Sign Cat 1 | Each | 20 |  |  | 0
15 | 16-20-c | Traffic Road Signs Category 3a | Each | 2 |  |  | 0
LANDSCAPING
1 | NS-1 | Development and maitinance (for 6 month) of Landscaping including sweet soil replacement (with unsuitble soil at site) leveling, dressing, fertilizers to all planted plnts (The plants and trees shuold be suitable for enviroment of Project area) and truff works complete in all respact as per directed by the Engineer. | LS / PS | 1 | 1000000 |  | 1000000
SUB Total of civil works (Internal Road)

## 23-Civil (Ext.RW)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 23: ROAD WORKS
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS (EXTERNAL ROAD)
Earthwork and Allied Activities
1 | 03-60 | Clearance of site by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, | M2 | 4950 |  |  | 0
2 | 03-65 | Compaction of Natural Ground | M2 | 4950 |  |  | 0
3 | 03-70-a | Formation of Embankment from Roadway Excavation in Rock Material requiring blasting and compaction Modified AASHTO 95% of embankment by power roller. | M3 | 4950 |  |  | 0
4 | 03-70-b | Formation of Embankment from Roadway Excavation in Rock Material requiring blasting and compaction Modified AASHTO 95% of embankment by power roller. | M3 | 4950 |  |  | 0
Sub Base, Base Course & Surfacing
5 | 16-04-b | Granular Sub Base Using Crushed Stone Aggregate | M3 | 754.3432 |  |  | 0
6 | 16-05-b | Water Bound Macadam Base Course | M3 | 754.3432 |  |  | 0
7 | 16-09-a | Bitumenous Prime Coat | M2 | 4950 |  |  | 0
8 | 16-14-a | Asphaltic Base Course (Asphalt Batch Plant Hot Mixed) (2" inch thick) (ABC) | M3 | 247.5 |  |  | 0
9 | 16-09-b | Bitumenous Tack Coat | M2 | 4950 |  |  | 0
10 | 16-14-b | Asphaltic Wearing Course (Asphalt Batch Plant Hot Mixed) (1½" inch thick) ( Wearing Course) | M3 | 198 |  |  | 0
Ancillary Works
S. No | MRS (2018) Reference | Description of Works | Unit | Quantity3 | Quantity4 | #N/A4 | #VALUE!34
11 | 16-73-a | Providing and fixing kerb stone (12"x18"x6") in cement sand mortar 1:3 in center media or round about as specified. | M | 500 |  |  | 0
12 | 16-76-a | Pavement marking in reflective chlorinated rubber paint with glass beads for line 15 cm width. | M | 275 |  |  | 0
13 | 16-25-a-01 | Supply and Fixing aluminium alloy road studs as per specs Large, strip 146x30mm, 171 beads: Uni-direction | Each | 100 |  |  | 0
14 | 16-20-a | Traffic Road Sign Cat 1 | Each | 5 |  |  | 0
15 | 16-20-c | Traffic Road Signs Category 3a | Each | 5 |  |  | 0
|  | Sub total of civil work (External Road) |  |  |  |  | 0

## 23A-Summary O&M
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 23A: Operation & maintenance of entire WTP & Client staff training
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | Operation & maintenance of entire WTP & Client staff training | 0
TOTAL AMOUNT RS |  | 0

## 23A-O&M
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 23A: Operation & maintenance of entire WTP & Client staff training
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
Operation & maintenance of entire WTP & Client staff training
S. No | MRS (2018) Reference | Description of Works | Column2 | #VALUE!2 | Column13 |  | Column34
1 |  | Operation and maintenance of entire WTP including provsion of staff as specified for operation and maintenance of plant training of the client's staff about the operation of the plant | Month | 3 |  |  | 0
SUB Total of O&M | [6 empty] | 0

## 24-Summery (SWDS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 24: STORM WATER DRAINAGE SYSTEM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 24-Civil (SWDS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 24: STORM WATER DRAINAGE SYSTEM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
Earth Work
1 | 03-67-b-i | Structural Excavation In Hard Rock Material by mechanical means requiring blasting | M3 | 660.05 |  |  | 0
2 | 03-67-b-ii | Structural Excavation In Medium Rock Material | M3 | 1980.15 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 1320.1 |  |  | 0
Plain and Reinforcement Concrete
4 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 193.27 |  |  | 0
5 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | M3 | 103.54 |  |  | 0
6 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 419.33 |  |  | 0
7 | 06-07-d-01 | Reinforced cement concrete work as in dams, spillways, weirs, barrages, cross drainage works and other hydraulic structures using crushed stone aggregate(screening & washing) and coarse sand i/c cost of all labour and material and all kinds of form works, moulds, shuttering lifting/pumping, curing, rendering and finishing the exposed surface, cast in situ/precast excluding the cost of steel reinforcement and labour for bending binding also excludig cost of additives which have to be paid separately. (1:1:2) | M3 | 563.34 |  |  | 0
8 | 06-25-j | Providing and fixing ribbed polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical (Walls/Columns) or horizontal (Floors/Slabs) expansion joints including cutting and jointing etc. complete in all floors . | M | 2635.5 |  |  | 0
Steel Reinforcement
9 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 108.16 |  |  | 0
|  | Surface Rendring |  | 0 |  |  | 0
10 | Ch-11 item 9 (b) P-75 | Cement plaster 1:5, upto 20' height 1/2" thick (Internal walls) | M2 | 0 |  |  | 0
11 | Ch-11 item 9 (c) P-75 | Cement Plaster 1:5, upto 20' height 3/4" thick (External walls) | Sq.m | 0 |  |  | 0
10 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 1320.1 |  |  | 0
11 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 1320.1 |  |  | 0
12 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 1320.1 |  |  | 0
13 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 1320.1 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 25-Summery (SCN)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 25: EXTERNAL SEWERAGE SYSTEM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 25-Civil (SCN)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 25: EXTERNAL SEWERAGE SYSTEM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-49-b | Excavation in open cut for sewers & manholes except shingle, gravel & rock : 2m to 5m | M3 | 247.5 |  |  | 0
2 | 03-51 | Excavation of trench in all kinds of soils except cutting in rock for pilelines upto 1.5m depth | M3 | 540 |  |  | 0
3 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 60 |  |  | 0
4 | 24-30-a-05 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects except excavation. (90 mm dia) PN-8 | M | 250 |  |  | 0
5 | 24-30-g-08 | Providing and installing HDPE bend 90mm dia | Each | 8 |  |  | 0
6 | 24-30-f-08 | Providing and installing HDPE Tee 90mm dia | Each | 10 |  |  | 0
7 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | M3 | 148.5 |  |  | 0
8 | 06-02 | Dry rammed shingle brick ballast or stone ballast 1.5" to 2" guage | M3 | 47.85 |  |  | 0
9 | 06-05-i | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:4:8) (septic Tank) | M3 | 20.5031 |  |  | 0
10 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 1.0935 |  |  | 0
11 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 5.4675 |  |  | 0
12 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | Tonne | 0.94478 |  |  | 0
13 | 14-37-b | Supply and Fixing cast iron (CI) manhole cover with frame etc (Heavey Type) of approved quality complete: 18" (455 mm) dia | Each | 3 |  |  | 0
14 | 23-01-c | Providing and laying R.C.C. pipe, moulded with cement concrete 1:1-1/2:3, with spigot, socket or collar joint, etc. including cost of reinforcement, conforming to B.S. 5911: Part-I, 1981 Class "L" including carriage, lowering in trenches to correc alignment and grade, jointing, cutting pipe where necessary, finishing and testing, etc. complete: 9" dia: | M | 150 |  |  | 0
15 | 23-11 | Soakage Pit (6'dia x 15' deep) complete | Each | 1 |  |  | 0
16 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 148.5 |  |  | 0
17 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 148.5 |  |  | 0
18 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 148.5 |  |  | 0
19 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 148.5 |  |  | 0
20 | 06-07-d-05 | MANHOLES
| 06-07-d-05 | Providing manhole size 24" x 18" (inside dimensions) as per approved design and specifications complete for 4" to 12" dia pipes upto 4 ft. (1.2 m) depth with 16" dia.Concrete Cover fixed in 4" thick RCC 1:2:4 slab (with 5 lbs per Cu.ft. or 80 kg/M3 of steel), burnt brick masonry walls 9" (225 mm) thick set in 1:3 cement sand mortar, 6" thick 1:3:6 cement concrete in foundation, 4" av. thickness 1:2:4 cement concrete in benching and 1/2" (13mm) thick cement sand plaster in 1:3 to all inside wall surfaces, channels and benching including making requisite number of main and branch channels but excluding the cost of excavation, back filling and disposal of excavated stuff. | Each | 6 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 26-Summary(FLood)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 26: FLOOD PROTECTION (EMBANKMENT)
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
TOTAL AMOUNT |  | 0

## 26-Civil(Flood)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 26: FLOOD PROTECTION (EMBANKMENT)
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-70-c | Formation of Embankment from Borrow Excavation in Common Material including compaction Modified AASHTO 90% by power roller. | M3 | 45210 |  |  | 0
2 | 03-48+03-29-a | Supplying clean and screened river or pit sand within 150m including removal of loose earth or overburden including Compaction of earth with power road roller 95% to 100% max. mod. AASHTO dry density | M3 | 8220 |  |  | 0
3 | 19-28-a | Providing and Laying stone pitching for top layer only : On slope | M3 | 9479.5089 |  |  | 0
| 19-15-a-01 | Supply & dump at site, without boat, including handling within 100m: boulders | M3 | 8220 |  |  | 0
4 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 41100 |  |  | 0
5 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 41100 |  |  | 0
6 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 41100 |  |  | 0
7 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 41100 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 27-Summery (SCADA)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 27: SCADA SYSTEM
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | INSTRUMENTATION AND CONTROL EQUIPMENT | 0
TOTAL AMOUNT RS |  | 0

## 27-Mechanical (SCADA)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 27: SCADA SYSTEM
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
INSTRUMENTATION AND CONTROL EQUIPMENT
A |  | INSTRUMENTATION AND CONTROL EQUIPMENT
1 |  | Design, Engineering, Supply & Installation of all items of SCADA system given below
CENTRAL CONTROL ROOM AT WATER TREATMENT PLANT
|  | Data Processing Servers | No. | 2
|  | Engineering work Station | No. | 1
|  | SCADA Operator Workstations including SCADA and HMI software | No. | 3
|  | 40" LED Display for Dynamic Mimic Board | No. | 1
|  | Laser A3 size color printer | No. | 1
|  | Fiber Optical Cable Termination Cabinet | No. | 1
|  | LAN Interface (IT Switch/Router) | No. | 2
DATA HIGHWAY
|  | Optical Fiber Cable as per plant requirement | M
AT WATER TREATMENT PLANT
|  | Programmable Logic Controller (PLC) | No. | 4
|  | Data Switching element (Router/Hub/Switch) | No. | 4
|  | Fiber Optical Cable Termination Cabinet | No. | 2
|  | Level Indicator Transmitter | No. | 35
|  | Ultrasonic Sludge Level Indicator | No. | 6
|  | PH Analyzer Meter | No. | 9
|  | Temperatue Indicator Transmitter with Thermowell | No. | 1
|  | Flow Indicator Transmitter with Totalizer | No. | 13
|  | Flow Transmitter with Totalizer | No. | 7
|  | Trubidity Sensor with Transmitter | No. | 9
|  | Flow Indicator | No. | 4
|  | Streaming Current Detector with Transmitter | No. | 4
|  | Pressure Indicator Transmitter | No. | 13
|  | Level Indicator | No. | 8
|  | Level Switch | No. | 8
|  | Pressure Indicator | No. | 28
|  | Motor Control Unit | No. | 60
|  | Residual Chlorine Sensor with Transmitter | No. | 2
|  | Motor operated Valve | No. | 22
|  | Flow Control Valve | No. | 1
2 |  | Testing & Commissioning Cost
3 |  | Operation & Maintenance Cost for 2 years
4 |  | Cost of Listed Spare Parts (for 2 years)
CENTRAL CONTROL ROOM AT WATER TREATMENT PLANT
|  | Data Processing Servers | No. | 1
|  | SCADA and HMI software | No. | 1
|  | 40" LED Display for Dynamic Mimic Board | No. | 1
|  | Laser A3 size color printer | No. | 1
|  | Fiber Optical Cable Termination Cabinet | No. | 1
|  | LAN Interface (IT Switch/Router) | No. | 1
DATA HIGHWAY
|  | Optical Fiber Cable as per plant requirement | M
AT WATER TREATMENT PLANT
|  | Programmable Logic Controller (PLC) | No. | 1
|  | Data Switching element (Router/Hub/Switch) | No. | 1
|  | Fiber Optical Cable Termination Cabinet | No. | 1
|  | Level Indicator Transmitter | No. | 2
|  | Ultrasonic Sludge Level Indicator | No. | 1
|  | PH Analyzer Meter | No. | 1
|  | Temperatue Indicator Transmitter with Thermowell | No. | 1
|  | Flow Indicator Transmitter with Totalizer | No. | 1
|  | Flow Transmitter with Totalizer | No. | 1
|  | Trubidity Sensor with Transmitter | No. | 1
|  | Flow Indicator | No. | 1
|  | Streaming Current Detector with Transmitter | No. | 1
|  | Pressure Indicator Transmitter | No. | 1
|  | Level Indicator | No. | 1
|  | Level Switch | No. | 1
|  | Pressure Indicator | No. | 2
|  | Motor Control Unit | No. | 2
|  | Residual Chlorine Sensor with Transmitter | No. | 1
|  | Motor operated Valve | No. | 2
|  | Flow Control Valve | No. | 1
5 |  | Training Cost
B | IP based Video Surveillance System (CCTV)
Supply, wiring, tagging, termination, design, installation, testing and commissioning of following system complete in all respects including all material, labor, tools, accessories etc. as per latest applicable international standards and technical specifications attached herewith
1 |  | 3 MPX/4MPX IP Based PTZ camera • Image Sensor : Day / Night 3 MPX CMOS sensor 1/2.8” • Optical Zoom : 30X • Lens Type : motor-zoom, auto-iris function • ONVIF Protocol Support : Profile S/Q • IR Range : 200 meter • 12 tours (maximum 32 presets each) •Video Intelligence Analytics • Bidirectional audio transmission • Built-in Heater and Fan • Minimum IP Class: IP66 | No. | 12
2 |  | IP Based Fixed Bullet Camera • Image Sensor : 5 MPX CMOS sensor 1/2.7” • Lens Type : motor-zoom, • IR Range : 50 meter • Frame Rate: 30 fps for 2592 x 1944, 60 fps for 1920 x 1080 • Multi-streaming • Compression : H.264+, H.265+, G.711 • Facial Recognition • Video Intelligence Analytics • Minimum IP Class: IP-67 with IK-10 rating • Memory Micro SD Card Slot up to 128 GB | No | 34
3 |  | 64 channels (NVR Network Video Recorder) • Resolution : 3840 x 2160 resolution (4K) (video + audio) • Stream Size: 256 Mb/s in total from all cameras; • Internal storage : 8 x HDD 3.5” 14 TB SATA (each) • Internal Alarm Input/Output: 8/4 relay type • Recording: Recording speed up to 960 fps • Recording and surveillance system: VMS (Video Management System) | No. | 1
4 |  | PTZ Controller | No. | 1
5 |  | Standard Pole 7 meter | No. | 17
6 |  | Access Switches • 24 x Ethernet 10/100/1000 Base-T ports, 4 x 1Gig SFP ports with 2 x 1G Single Mode SFP • POE/POE+ • Switching capacity at-least 200Gbps or higher | No | 1
7 |  | 8 Port Access Switch POE with SFP Ports | No. | 10
8 |  | Work Station with Client Software (Core i7 Ultra Slim Desktop PC with Genuine, latest Windows 10 Prof 64bit, 8, 2TB HDD & DVD Writer) for all Systems including Keyboard & mouse. | No | 1
9 |  | UTP CAT-6, 23AWG Cable for Data Communication System from Communication Rack to each node/ outlet in 25 mm PVC conduit / channel including termination and tagging at both ends. Complete in all respects. | m | 1280
10 |  | Communication Rack 12U (Wall Mounted) , Complete with vertical cable managers. Rack shall be equipped with power distribution units (PDUs) with imported power sockets etc. Complete in all respects. • 3 no. cooling fans • Steel front door • Earthing strip • Door lock | No | 1
11 |  | Patch Cord CAT-6, 1 meter and 3 meter (for 16 nodes) | No. | 16
12 |  | 24 Core Fiber Optic Cable , Standard G652-D, • Cable type Single Mode • Cable construction Loose tube • Layer of Aramid Yarn 5mm • Wavelength 1300/1550 nm • Max attenuation 0.36 db/km Excavation duct price with all accessories shall be included | m | 1545
13 |  | 24-Port ODF with coupler, pigtails and Patch cords, complete accessories. Housing Material :Steel | No | 17
14 |  | HDPE pipe • size 40mm • outer dia 40mm • wall thickness 3.5mm • standard length: 125m/250m/1000m | m | 2900
15 |  | 2 kVA UPS Including -Pure Sine wave -Power Cable from control room to Access Switch -Complete in all respect | No | 1
16 |  | Gell VRLA Battery Backup for 4 HOUR • High temperature tolerance • Excellent for deep discharge • Hugh resistance to water loss • Maintenance free operation • Spill proof construction | Job | 1
17 |  | Installation, Programming, Testing and Commissioning of complete system including cable trays, Stainless steel pipe/ Stainless steel flexile pipe. | Job | 1 | Included in above |  | Included in above
SUB TOTAL OF (INSTRUMENTATION AND CONTROL EQUIPMENT)

## 28-Summary (BFP-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 28: BELT FILTER PRESS SLUDGE PUMPING STATION
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
3 | ELECTRICAL WORKS | 0
TOTAL AMOUNT RS |  | 0

## 28-Civil (BFP-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 28: BELT FILTER PRESS SLUDGE PUMPING STATION
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-b-ii | Structural Excavation in Common Material by mechanical means | M3 | 105.8 |  |  | 0
2 | 07-30 | Supplying and filling sand under floor or plugging in wells | M3 | 38.28 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 52.9 |  |  | 0
4 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 16.5 |  |  | 0
5 | 06-07-d-01 | Reinforced cement concrete work as in dams, spillways, weirs, barrages, cross drainage works and other hydraulic structures using crushed stone aggregate(screening & washing) and coarse sand i/c cost of all labour and material and all kinds of form works, moulds, shuttering lifting/pumping, curing, rendering and finishing the exposed surface, cast in situ/precast excluding the cost of steel reinforcement and labour for bending binding also excludig cost of additives which have to be paid separately. (1:1:2) | M3 | 25.83 |  |  | 0
6 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 25.83 |  |  | 0
7 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 21.24 |  |  | 0
8 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 139.98 |  |  | 0
9 | 07-05-a-03 | 1st class brick work in ground floor Cement, sand mortar 1:4 | M3 | 34.94 |  |  | 0
10 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | M2 | 174.72 |  |  | 0
11 | 11-21-a-03 | Distempering New surface : Three coats | M2 | 174.72 |  |  | 0
12 | 11-18-b | Cement pointing struck joints, on walls, upto 20' height : Ratio 1:3 | M2 | 174.72 |  |  | 0
13 | 11-10-a | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:2) | M2 | 174.72 |  |  | 0
14 | 10-22-a | 1.5" thick mosaic flooring, including rubbing & polishing complete : Using grey cement | M2 | 46 |  |  | 0
15 | 10-41-a-02 | Mosaic dado or skirting complete as per specs Using grey cement : 1/2" thick | M2 | 46 |  |  | 0
16 | 09-01 | First class tile roofing including earth, mud plaster, gobri leeping, cement plaster etc complete | M2 | 104.16 |  |  | 0
17 | 09-13 | 2 coats of bitumen laid hot using 34 lbs. for %sft over roof & blinded with sand at 1 cft per % sft | M2 | 104.16 |  |  | 0
18 | 06-28 | Providing and laying polythene sheet 0.005" thick (0.05mm 500gauge) under cement concete. | M2 | 104.16 |  |  | 0
19 | 25-39-a-02 | Providing and fixing steel windows with openable glazed pannels, using beam section for frame 1-1/2" x 1" x 5/8" x 1/8", z-section for leaves 3/4" x 1" x 3/4" x 1/8", T- section sashes 1"x1"x1/8" glass panes, wooden screed for glazing embded over a thin layer of putty duly screwed with leaves, brass fittings holdfast, duly painted, complete in all respects, including all cost of material and labour etc. as per approved design and as directed by the engineer - in -charge Glass pane 2.5mm thick | M2 | 14.4 |  |  | 0
20 | 25-45-b | Supplying and Fixing 18 SWG MS Sheet Gate with angle iron frame (2"x2"x3/16") with side window, lock, painting etc | M2 | 14.4 |  |  | 0
21 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 52.9 |  |  | 0
22 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 52.9 |  |  | 0
23 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 52.9 |  |  | 0
24 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 52.9 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 28-Mech (BFP-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 28: BELT FILTER PRESS SLUDGE PUMPING STATION
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Sludge Pumps
Providing, installing, testing and commissioning Sludge Pumps (end-suction, non-clogging/solids-handling, screw type, Min Free Passage Size: 15-50 mm), of internationally reputed approved make, complete with pump, 3-phase induction motor (4-pole, Efficiency class IE3), spacer coupling, support base/frame, pressure gauges (on suction and discharge sides), mechanical seal, temperature & vibration monitoring devices, automatic liquid level-controlled switching device (ultrasonic sensor type), motor control unit (MCU, in painted metallic box, complete with auto star-delta starter and all the required control, relay, monitoring and protection devices)and electrical & control cables (between motor and MCU), with pump impeller, shaft & sleeve to be of stainless steel of approved grade, including all jointing, fixing & installation accessories, vibration-control accessories, initial lubricant charge, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Sludge Feeding Pump (Max Concentration: 5 %) Capacity: 15m3/h, Head: 20 m | No | 4 |  |  | 0
2 | NS-2 | Flow Meter
|  | Providing, installing, testing and commissioning Water Flow Meter (Electromagnetic type, Range: 0 to 2000 m3/h, Accuracy: ± 0.5%, PN 16, Max Water Temperature: 40OC) on pipeline (HDPE, DN 150), of internationally reputed approved make, complete with meter, relays,on-site LCD display unit (with adjustable backlight and contrast)& its mounting arrangement (in stainless steel, Grade 316), display unit cabinet (painted metallic box with glazed front door), all the necessary provisions, instruments and accessories for integration with SCADA and power supply, including all jointing, fixing & installation accessories, all painting & coatings and a complete set of special tools, test equipment & essential spare parts, complete in all respects, in accordance with the Contract | No | 4 |  |  | 0
3 | NS-3 | DUCTILE IRON PIPE (DI PIPE)
Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron Pipe class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
|  | DI Pipe 150mm | m | 30 |  |  | 0
4 | NS-4 | Providing at site, laying, cutting, fixing, jointing, testing and commissioning Ductile iron (cast on flange) specials (such as bend, tee, cross collar, reducer, tail piece, flanged spigot, cap, flanged socket, taper, angle branch, plug etc) class-K12 conforming to specifications (ISO2531 and BS 4772) and relevant ANSI/AWWA standards with all accessories, Nut, Bolts, washers, jointing material and lubricants complete in all respect as per drawings and specifications.
a) |  | Bend 90°
|  | 150 mm | No | 16 |  |  | 0
b) |  | DI TEE
|  | 150mm x 150mm | No | 6 |  |  | 0
c) |  | DI REDUCER
|  | 150mm | No | 4 |  |  | 0
5 | NS-5 | (CI) Check Valves ( 150mm )
|  | Providing, installing and testing cast iron (CI) Check Valves (Swing type, Flanged, BS 5153, PN 10) on pipelines, of internationally reputed approved make, including gaskets, steel nuts & bolts and other jointing accessories, with all the exposed ferrous surfaces to be epoxy coated, complete in all respects, in accordance with the Contract, as follows: | No | 8 |  |  | 0
6 | NS-6 | SLUICE VALVE ( 150mm )
|  | Sluice Valves with all acessories complete in all respect for various pipe sizes as shown on the drawings | No | 8 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0
Note on C16: Author: HDPE pipe and fittings should be taken

## 28-Electrical (BFP-PS)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 28: BELT FILTER PRESS SLUDGE PUMPING STATION
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
ELECTRICAL WORKS
A.01 |  | Light Circuits
Supply, installation and commissioning of light circuit wiring, to be wired with 4x2.5mm sq. (1P+1N+1UPS+1PE) PVC insulated 300/500 V grade wire make Pakistan Cable, Newage,AGE Cables,Golden Star, in and including cost of 1” dia. heavy duty PVC conduit make Beta , Popular recessed in , walls, Roof slab, or on surface or above false ceiling or as required as per site conditions, all PVC conduit accessories, pull boxes, steel pull wires , complete in all respects. Each circuit shall have independent PE.
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 146.34 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 73.17 |  |  | 0
A.02 |  | 1-Light Point Controlled By One Switch
Wiring of one light point controlled by one switch and wired with 3x1.5 mm sq. (P+N+PE) PVC insulated wires 300/500 V. grade make Pakistan Cable, Newage Pioneer Cables,, in and including cost of 3/4" dia. heavy duty PVC conduit make Beta , Popular installed on RCC slab, above false ceiling, recessed in wall, columns slabs or above light carrier all PVC conduit accessories, 3" high PVC junction boxes, pull boxes, steel pull wires, PVC flexiable conduit from ceiling junction box to light fixture flush type plate switches, including cost of back boxes and switches of 10 Amps.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 256.1 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 170.73 |  |  | 0
A.03 |  | Point -Point Wiring
Same as per item No. A.02 but Loop wiring of a light point from first light point on same switch circuit, complete in all respects.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 268.3 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 178.87 |  |  | 0
A.04 |  | Gang Light Control Switches
| 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
| 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 2 |  |  | 0
| 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | Each | 4 |  |  | 0
A.05 |  | Exhaust Fan Point
Same as Item No. A.02 mentioned above but wiring of exhaust fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 54.88 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 36.59 |  |  | 0
A.06 |  | Ceiling Fan Point
Same as Item No. A.02 mentioned above but wiring of Ceiling fan point including cost of 10 Amp switch with M.S box 16 SWG with earth terminal.
| 15-05-a | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 3/0.029" 1/2" i/d | M | 82.32 |  |  | 0
| 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | M | 54.88 |  |  | 0
A.07 |  | 1-3 pin switch & plug combined recessed type :10/15 Amp
Supply and wiring of one 3 pin switch & plug combined recessed type :10/15 Amp outlet point from distribution board with single core 2x4mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling, all conduits accessories, junction boxes, pull boxes etc. 2.5mm2 cable as PC excluding cost of 3 pin 13 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 109.76 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 73.17 |  |  | 0
A.08 |  | Loop-Loop- 3 pin switch & plug combined recessed type :10/15 Amp
Same as item No.A.12 above but loop wiring of 3 pin switch & plug combined recessed type :10/15 Amp outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 146.34 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 97.56 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 195.12 |  |  | 0
| 15-20-b | Supply and Erection 3 pin switch & plug combined recessed type :10/15 Amp | Each | 14 |  |  | 0
A.09 |  | Loop-Loop- 5 Amps Switch Socket
Same as item No.A.12 above but loop wiring of 5A power socket outlet with 2x4mm2(P+N) & 1x2.5mm2 as CPC from point to point excluding cost of one 15A 3 pin switch socket outlets with make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel boards recessed in walls /columns.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 256.1 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 170.73 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 341.47 |  |  | 0
| 15-20-a | Supply and Erection 3 pin switch & plug combined recessed type : 5 Amp | Each | 14 |  |  | 0
A.10 |  | 1-20 Amps Switch Socket
Supply and wiring of one 3pin 20 Amps Power plug socket outlet point from distribution board with single core 2x6mm2(P+N) PVC insulated 300/500 volt grade cable in & including PVC conduit recessed in walls/R.C.C. slab, or installed on surface of Ceiling including all conduits accessories, junction boxes, pull boxes etc. 4mm2 cable as PC including cost of 3 pin 20 Amps switch & socket out let make CLIPSAL / MK / Legrand / ABB or approved equivalent installed on & including 16 SWG sheet steel board recessed in walls complete in all respects and as per specifications & drawings.
| 15-05-d | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.036" | M | 73.18 |  |  | 0
| 15-05-c | Supply and Erection single core PVC insulated copper conductor 250/440 V grade cable : 7/0.029" | M | 48.79 |  |  | 0
| 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | M | 97.57 |  |  | 0
| 15-81 | Supply and Fixing 20 Amp power plug | Each | 4 |  |  | 0
A.11 |  | Fitting and Fixtures.
Supply at site, installation, testing and commissioning of the following indoor incandescent/LED light fittings, complete with brass lamp holders, fixing accessories, earthing terminal, drivery circuitry make as specified or by any one of the manufacturers mentioned in Annexure-”A”, complete in all respects.
i) | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lm, as per instruction of Engineer, surface mounted circular shape or equivalent. | Nos. | 12 |  |  | 0
iii) | 15-36-i-15 | Supply, installation, testing and commissioning of recessed Dawn Light of best quality with CFL (13-17 watt) Energy saver and with Glass Reflector | Nos. | 24 |  |  | 0
iii) | 15-36-k-03 | Supply, installation, connecting, testing and commissioning of Wall mounted Bulkhead light fixtures with LED retrofit lamp 540 Lumens output, complete in all respects | Nos. | 8 |  |  | 0
A.12 |  | Exhaust Fans
a) | 15-69-b | Supply and Erection best quality exhaust fan complete with shutter & regulator : 16"sweep | Nos. | 4 |  |  | 0
A.13 |  | Ceiling Fan
| 15-127-m | Supply at site, installation, testing and commissioning of Fan Dimmer with switch/ MS, powder coated back box with all associated accessories, complete in all respects. | Nos. | 4 |  |  | 0
| 26-01-l-01 | Supply and Erection of AC Energy Efficient Ceiling Fans 56 inch, 50 W | Nos. | 8 |  |  | 0
A.14 |  | Wall Bracket Fan
| 15-68-e | Supply, installation, testing & commissioning of Direct axial Wall Bracket fan | Nos. | 2 |  |  | 0
A.15 |  | PVC Conduit
Supply at site of PVC conduit heavy duty to be concealed in RCC slabs, walls, floor, columns above false ceiling or as required as per site conditions including cost of all PVC conduit accessories, steel pull wires, complete in all respects.
i) | 15-02-b-08 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 4" i/d | M | 18.3 |  |  | 0
A.16 |  | Distribution Board
Fabrication, supply at site, installation, testing, commissioning and connections of wires / cables of Distribution Boards “Light / Power” concealed / open type to be installed as and where shown on drawing, made of MS sheet 16 SWG degreased and derusted, zinc phosphated, finished with electro-static powder coating of 50 micron thickness in approved colour, DB housing to comply with protection class IP-44 with hinged door, flexible earthing strap lockable handle, catcher, earthing bar, neutral strip, internal wiring from MCBs terminating on cable terminal blocks, including cost of all necessary materials complete in all respects. DBs shall be manufactured by any one of the manufacturers as mentioned in List.
| 15-162-j | Supply, Installation, connecting, testing & commissioning of wall mounted DBLP-G1, DBLP-F1, Distribution Boards, complete with all metering with indication lamps complete in all respects, as per SLD. | Each | 2 |  |  | 0
A.17 |  | Non-maintained Emergency Lighting
| Appendix ' c' Page No-5 | Supply, installation and connections of Self Test Maintained With ISO 7010 Legend Set 7 Watt Colour Temperature 6000K ,235 Lumens on main supply and 150 Lumens on battery, Avg. Rated Life (Hrs) 30000 hr, IP65 rating with hanging arrangment on wall or ceiling as required complete in all respect as approved by the engineer incharge make Delpro (uk) or eqv. | Nos. | 1 |  |  | 0
SUB TOTAL OF ELECTRICAL WORKS | [6 empty] | 0

## 29-Summery(BFP)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA:
LOT 1: WATER TREATMENT PLANT
SUMMARY OF BILL NO. 29: BELT FILTER PRESS UNIT
BILL NO. | DESCRIPTION OF WORK | Amount (PKR)
1 | CIVIL WORKS | 0
2 | MECHANICAL WORKS | 0
TOTAL AMOUNT |  | 0

## 29- Civil MRS (BFP)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 29: BELT FILTER PRESS UNIT
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
CIVIL WORKS
1 | 03-67-b-i | Structural Excavation In Hard Rock Material by mechanical means requiring blasting | M3 | 105.95 |  |  | 0
2 | 03-67-b-ii | Structural Excavation In Medium Rock Material | M3 | 317.86 |  |  | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | M3 | 296.67 |  |  | 0
4 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) | M3 | 1.2 |  |  | 0
5 | 06-07-a-01 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:1:2) | M3 | 35.67 |  |  | 0
6 | 06-07-b-01 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. (1:1:2) | M3 | 45.29 |  |  | 0
7 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 104.35 |  |  | 0
8 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | M3 | 296.67 |  |  | 0
9 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. | M3 | 296.67 |  |  | 0
10 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5 km. upto 8 km. | M3 | 296.67 |  |  | 0
11 | 03-20-d | Transportation of earth all types for every 1 km extra lead or part thereof beyond 8 km. | M3 | 296.67 |  |  | 0
SUB TOTAL OF CIVIL WORKS | [6 empty] | 0

## 29-Mech(BFP)
GOVERNMENT OF KHYBER PAKHTUNKHWA
KHYBER PAKHTUNKHWA CITIES IMPROVEMENT PROJECT
LOCAL GOVERNMENT, ELECTIONS AND RURAL DEVELOPMENT DEPARTMENT
KPCIP-CW-04: MINGORA GREATER WATER SUPPLY SCHEME INCLUDING NEW WATER TREATMENT PLANT (WTP), INTAKE STRUCTURE, TRANSMISSION, AND DISTRIBUTION SYSTEMS AND SCADA: LOT 1: WATER TREATMENT PLANT
BILL OF QUANTITIES
BILL NO. 29: BELT FILTER PRESS UNIT
Item No. | REF. Nos CH/Item | Description of Items | Unit | Quantities, Unit Rate and Amount
|  |  |  | Qty | Unit Rate (PKR) | Unit Rate (Rs) in Words | Amount (PKR)
MECHANICAL WORKS
1 | NS-1 | Filtration Unit
|  | Providing, installation, testing & commissioning Belt Press Filter , in stainless steel AISI 316L construction and including the control installation for the belt tracking, tensioning and washing systems complete in all respect s as per drawings and specifications. | No. | 4 |  |  | 0
Capacity: 15 m3/h, Inflow Solid Content: 2-5%, Dry Solid Content: 15 - 20%
2 | NS-2 | Conical Mixers
|  | Providing, installation, testing & commissioning of conical mixers, design & construction in stainless steel AISI 316 construction for the continuous and homogeneous sludge-polymer mixing. Designed to install at the sludge feeding pump outlet, complete in all respect s as per drawings and specifications. | No. | 4 |  |  | 0
3 | NS-3 | Control Panel
|  | Providing, installation, testing & commissioning control panel to operate the belt press and quoted/included auxiliaries of the belt press and related equipment. The control panel includes the described components and is complete in all respects as per drawings and specifications. | No. | 4 |  |  | 0
4 | NS-4 | Belt Washing Pumps
Providing, installation, testing & commissioning Belt Washing Pumps (high pressure,vertical-shaft, non-clogging/solids-handling, submersible, centrifugal type), of internationally reputed approved make, complete with pump, motor (4-pole), automatic liquid level-controlled switching device (ultrasonic sensor type) and starter, with pump impeller, shaft & sleeve to be of stainless steel of approved grade, suitable for the belt press and belt thickener washing process, 7.5 kW operation power at 10 bar pressure, including all jointing, fixing & installation accessories, all painting & coatings; and a complete set of special tools, test equipment & spare parts, complete in all respects, in accordance with the Contract, as follows:
|  | Pumps Capacity:20m3/hr | No | 4 |  |  | 0
SUB TOTAL OF MECHANICAL WORKS | [6 empty] | 0